| NOGRR Number | 124 | NOGRR Title | Additional VRT Requirement for IRRs |
| --- | --- | --- | --- |

| Date | November __, 2013 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Jeff Billo / Shun-Hsien (Fred) Huang |
| E-mail Address | Jeff.Billo@ercot.com / shuang@ercot.com |
| Company | ERCOT |
| Phone Number | (512) 248-6334, (512) 248-6665 |
| Cell Number |  |
| Market Segment | ERCOT |

Comments

ERCOT provides these additional comments to address WGR developer concerns that applying the HVRT standard to IRRs that had not synchronized with the ERCOT system by August 30, 2013 is unnecessary.

The revisions proposed in this comment revert to the original proposal to grandfather IRRs based on whether the Standard Generation Interconnection Agreement (SGIA) was signed on or before August 30, 2013.  However, to guard against the possibility that an SGIA for a grandfathered IRR could be amended to provide for a different (potentially substandard) turbine model and thereby introduce unanticipated stability risk, ERCOT proposes a clarification that the HVRT standard would apply to any otherwise grandfathered IRRs that interconnect a different turbine model than the model described in the SGIA.

Revised Cover Page Language

None.

Revised Proposed Guide Language

2.9.1	Additional Voltage Ride-Through Requirements for Intermittent Renewable Resources

(1)	All Intermittent Renewable Resources (IRRs) shall also comply with the requirements of this Section, except as follows:

(a)	An IRR that interconnects to the ERCOT System pursuant to a Standard Generation Interconnection Agreement (SGIA) executed before August 30, 2013 is not required to meet any high Voltage Ride-Through (VRT) requirement greater than 1.1 per unit voltage unless the interconnected IRR includes one or more turbines that differ from the turbine model described in the SGIA (including any attachment thereto), as that agreement existed on August 30, 2013.

(b)	An IRR that interconnects to the ERCOT System pursuant to an SGIA executed prior to November 1, 2008 is not required to meet VRT requirements presented in this Section.  However, any IRR that is installed on or after November 1, 2008 and that interconnects to the ERCOT System pursuant to an SGIA executed before August 30, 2013 (except for an IRR installed pursuant to an SGIA executed before November 1, 2008) shall be VRT-capable in accordance with the low VRT requirements in this Section and high VRT requirements in this Section up to 1.1 per unit voltage.  Any IRR that interconnects with the ERCOT System on or after August 30, 2013 (except for an IRR installed pursuant to an SGIA executed before August 30, 2013) shall be VRT-capable in accordance with all VRT requirements in this Section.

(c)	Notwithstanding any of the foregoing provisions, an IRR’s VRT capability shall not be reduced over time.

(2	)	Each IRR shall provide technical documentation of VRT capability to ERCOT upon request.

(3)	Each IRR is required to set generator voltage relays to remain in service for at least 0.15 seconds during all transmission faults and to allow the system to recover as illustrated in Figure 1, Default Voltage Ride-Through Boundaries for IRRs, below.  Recovery time to 90% of per unit voltage should be within 1.75 seconds.  Faults on individual phases with delayed clearing (zone 2) may result in phase voltages outside this boundary but if the phase voltages remain inside this boundary, then generator voltage relays are required to be set to remain connected and recover as illustrated in Figure 1.

(4)	Each IRR shall remain interconnected during three-phase faults on the ERCOT System for a voltage level as low as zero volts with a duration of 0.15 seconds as measured at the Point of Interconnection (POI) unless a shorter clearing time requirement for a three-phase fault specific to the generating plant POI is determined by and documented by the TSP in conjunction with the SGIA.  The clearing time requirement shall not exceed nine cycles.

(5)	Each IRR shall set generator voltage relays to remain interconnected to the ERCOT System during the following high-voltage conditions, as illustrated in Figure 1: 1.2 per unit voltage for up to 0.2 seconds, 1.175 per unit voltage for up to 0.5 seconds, and 1.15 per unit voltage for up to 1.0 seconds.  The indicated voltages are measured at the POI.

(6)	An IRR may be tripped Off-Line after the fault clearing period if this action is part of an approved Special Protection Systems (SPSs).

(7)	VRT requirements may be met by the performance of the generators; by installing additional reactive equipment behind the POI; or by a combination of generator performance and additional equipment behind the POI.  VRT requirements may be met by equipment outside the POI if documented in the SGIA.

(8)	If an IRR fails to comply with the clearing time or recovery VRT requirement, then the IRR and the interconnecting TSP shall be required to investigate and report to ERCOT on the cause of the IRR trip, identifying a reasonable mitigation plan and timeline.

Figure 1:  Default Voltage Ride-Through Boundaries for IRRs.