- ERCOT ISO

- ICCP Network Interface Control Document (NICD)

Version 1.1

November 29, 2000

- Document Revision History

| Revision Date | Version Number | Revised by | Revision Description |
| --- | --- | --- | --- |
| 11/18/00 | 1.0 | F. Kendall | First publication. |
| 11/28/00 | 1.1 | F. Kendall | The format of the Bilateral Table Name has been revised. Terminology related to the Bilateral Table has also been improved. |

1.	Introduction	1

1.1	User Prerequisites	1

1.2	References	2

1.3	ICCP NICD Organization	2

1.4	Document Update Policy	3

1.5	Document Conventions	4

1.6	Glossary	4

2.	Network Topology Overview	7

2.1	Wide Area Networks	7

2.2	Participant’s Site WAN Connections	8

3.	ICCP Connections	9

3.1	Establishing ICCP Associations	9

3.2	Association Restrictions (Peer Communication)	12

3.3	Association Identifiers	12

3.4	Protocol Selectors	13

3.5	TCP Port Number	13

3.6	System Connections	13

4.	ICCP Certification Testing	15

5.	ICCP Protocol	17

5.1	Supported Features	17

5.2	ICCP Version	17

5.3	Bilateral Tables	17

5.3.1	Bilateral Table Names	18

5.3.2	Bilateral Table Version Management	18

5.4	ICCP Conformance Blocks	20

5.5	ERCOT MMS PDU Size	20

5.6	Domain Naming Standard	21

5.7	Data Set Naming Standard	23

5.8	ERCOT Defined ICCP Objects	24

5.8.1	Data Object Naming Standard	24

5.8.2	ERCOT ICCP Objects	25

5.9	Transfer Set Definition Standards	27

5.10	Data Quality	29

6.	Real-Time Data Semantics	31

6.1	Status Values	31

6.2	Energy and Reactance Values	31

- List of Figures

Figure 2.1 Network Topology Overview	7

Figure 2.2 Participant Site Connections	8

Figure 3.1 Network Protocol Suite	9

Figure 3.2 Types of Associations	10

Figure 3.3: Single-use Association (ERCOT Server)	11

Figure 3.4: Single-use Association (Participant Server)	11

- List of Tables

Table 1.1: Definitions	4

Table 3.1: AP Title Format	12

Table 5.1 Required ICCP Supported Features	17

Table 5.2 Validity Quality Code Definitions	20

Table 5.3 Current Source Quality Code Definitions	20

Table 5.4 Normal Source Quality Code Definitions	20

Table 5.5 Normal Value Quality Code Definitions	20

Table 6.1 Status Value Semantics	20

Table 6.2 Energy and Reactance Values	20

# Introduction

The ERCOT ICCP Network Interface Control Document (ICCP NICD) sets forth the standards, conventions, and fundamental parameters required for ERCOT Participants to exchange data with ERCOT using the ICCP protocol.

Information provided in this NICD is important to both the Participant and the Participant’s ICCP vendor. The NICD specifies important configuration and functional requirements for ICCP implementations so that the Participant’s system will interoperate with ERCOT’s system. Vendors will need this information to include the required features and to build the proper delivered ICCP configuration. Such information includes addressing specifications, naming conventions, required ICCP Conformance Blocks, and required features of the specified Conformance Blocks. Standards are also specified for the interpretation of data values exchanged, and well as quality code semantics.

The NICD also includes standards for units of measure, value semantics, and data object naming conventions. This information is needed by Participants in order to exchange the correct values between the Participants’ EMS/SCADA systems and the ICCP subsystem.

## User Prerequisites

Anyone using this document should have:

- A general knowledge of data communications concepts

- A working knowledge of Energy Management System functions and concepts

- Familiarity with modern data communications technology

- Knowledge of ICCP concepts

- Knowledge of the TCP/IP protocol concepts

- General knowledge of the International Standards Organization’s Open System Interconnection model.

Additionally, the Participant should be familiar with the ERCOT Network and have a general knowledge of their own local EMS/SCADA System.

## References

The references are listed here in two sections. The References to Standards section is primarily for those interested in delving deeper into ICCP technology. A study of these sources is not essential to the Participant’s ability to operate an ICCP node. It is assumed that the Participant’s ICCP vendor is familiar with the standards referenced in this section.

The ERCOT Publications section refers to documents that should be considered as essential supplements to this NICD.

References to Standards:

- IEC 870-6-503 Tase.2 Services and Protocol Version 1996-08

- IEC 870-6-702 Tase.2 Functional Profile Version 1996-11

- IEC 870-6-802 Tase.2 Object Models Version 1996-08

- ICCP User's Guide (EPRI TR-107176, RP4379-01) - Final Report, December 1996

- RFC 791 Internet Protocol (IP)

- RFC 793 Transport Control Protocol (TCP)

- RFC 1918 Address Allocation for Private internets

ERCOT Publications:

- ERCOT ICCP Test Plan

- Communicating with ERCOT

- Association Information Exchange Form (AIEF)

## ICCP NICD Organization

The NICD contains the following information:

Section 1, Introduction, presents the purpose and scope of the NICD.  Also included are references to other documents, document formatting conventions, document update procedures, and a limited glossary.

Section 2, Network Topology Overview, provides a brief description of the ERCOT WAN and the Participant’s WAN connection.

Section 3, ICCP Connections, discusses the standards and requirements for configuring, physically connecting, and establishing logical connections between Participants and ERCOT.  This section also includes a short description and reference to ICCP Certification testing.

Section 4, ICCP Certification Testing, identifies the purpose of the certification test and references the test documents.

Section 5, ICCP Protocol, specifies the standards, conventions, parameters, and requirements for a Participant’s configuration of ICCP Application Service Elements.  ICCP object naming conventions are also included.

Section 6, Real-Time Data Semantics, describes the allowable values and units of measure.

## Document Update Policy

ERCOT is responsible for keeping this document current.  Periodic document revisions are posted to the TexasChoiceProgram web site.  Announcements of NICD revisions will be provided according to the normal ERCOT announcement procedures.

The page following the title page contains the Document Revision History.  This table defines each revision number, its date, identifies the primary editor of the revision, and provides a general description of the changes made. The document file name on the web site includes the latest revision number. The revision number and revision date is also shown on the NICD title page.

The document revision number is in the form Version x.y, where x is the major version number and y is the minor version number.  The minor version number changes whenever there is any update to the document.  The major version number changes only when there is a significant content change.  For example, the addition or deletion of new policies, requirements, protocols, or significant conventions will result in the major version number being incremented, and the minor version number being reset to zero.  This also applies to the addition or deletion of whole ICCP conformance blocks, or other major functions.  Changes such as the addition of ICCP messages, units of measure, or the expansion of existing policies, conventions, and requirements result in changing only the minor version number.  In short, the major version number should alert Participants to a change that may have a programmatic impact to their systems, rather than simply configuration changes.

## Document Conventions

To enhance readability, a few simple formatting conventions are used in the NICD. Data formats and information specifications are presented in the form of both variable data and fixed constants. The following font attribute conventions are used in the NICD:

Variable fields display placeholders for values to be filled in with data that dependends on the Participant’s system.  Variable data is shown in this format.

Fixed constants are fields whose values are defined and do not change from system to system.  Constant values are shown in this format.

Some sections may lack detail that is being developed for inclusion in the NICD, but not available as of the publication date. To avoid publication delay, comments are entered in this box style providing a summary of the information to be included and the anticipated NICD version in which the information will appear. This is essentially a “TBD” comment.

The NICD has been formatted for double-sided printing. Users are encouraged to take advantage of this document characteristic. The NICD can also be printed using single-sided printing yielding high-quality results.

Although most of the document is in black & white, a number of illustrations are presented in color to facilitate the idea being illustrated. The color illustrations may not render well if printed in black & white. Color illustrations have been kept to a minimum so that document production on paper will not be a major effort. Color renditions can be obtained most efficiently by printing the entire NICD on a black & white printer such as a laser printer, then printing only the few pages with color illustrations on a color printer. The illustrations are listed separately in the Table of Contents under List of Figures.

## Glossary

Table 1.1: Definitions

| Terms | Definitions |
| --- | --- |
| AIEF | Association Information Exchange Form. A form used to exchange addressing and naming assignment information between ERCOT and a Participant. This form facilitates establishing the ICCP connection. |
| Application Process | The sequence of events that a Participant executes to indicate its desire to communicate with ERCOT and exchange essential system information. The sequence begins by submitting the forms provided as attachments to the document entitled Communicating with ERCOT, and subsequently exchanging the information on the AIEF. |
| ERCOT Private Network (also called Frame Network and DACS Network) | A Wide Area Network dedicated to the exchange of data between ERCOT and its Participants. The ERCOT Private Network is managed and operated by one or more public network service providers. The particular providers may change from time to time. Although the physical network carries traffic for many of the providers’ customers (of whom ERCOT is one) the circuits (called PVCs) are dedicated to ERCOT and carry no traffic other than that produced by ERCOT and its Participants. These dedicated circuits are provisioned with dedicated bandwidth allocations. Therefore, the circuits in the “public” network carrying ERCOT traffic create a Private Network in the same sense as the entire network being physically dedicated to ERCOT. |
| ICCP | Inter-control center Communication Protocol. Also called Telecontrol Application Service Element 2 (TASE.2). The international standard protocol for data exchange among utilities. ICCP is the protocol specified in this NICD. |
| Permanent Virtual Circuit (PVC) | A permanently commissioned circuit between two communicating entities. A PVC is commissioned on a Frame Relay network by allocating a specified minimum number of time slots in an extremely wide-band multiplexing scheme. The PVC is defined by addresses assigned to the Frame Relay access ports at each end of the circuit. A Frame Relay address is called a Data Link Circuit Identifier (DLCI). PVC bandwidth is a flexibile allocation of the minimum data rate combined with agreed-upon rate increases as needed. |

# Network Topology Overview

## Wide Area Networks

The ERCOT network is designed for high reliability and performance. Figure 2.1 provides a simplified illustration of the network topology.

Figure 2.1 Network Topology Overview

It can be seen from the topology that a high degree of redundancy is designed into the network.  Circuit failures occurring within the Frame Relay or DACS networks will cause automatic rerouting of data paths due to the operation of the routers.  Although a WAN circuit failure will cause loss of an active Association, the routers will reestablished new data paths quickly so that the lost Association can be reopened without the Participant’s system having to select alternate addresses.  Association establishment standards and procedures are discussed in Section 3.

## Participant’s Site WAN Connections

Figure 2.2 illustrates the equipment complement installed at the Participant’s site that provides the connection between the Participant’s ICCP node and ERCOT. Recognizing that several LAN connection architectures are possible, the illustration represents one of the simplest.

Figure 2.2 Participant Site Connections

The WAN connection design supports a robust Participant LAN architecture such as redundant ICCP nodes connected to redundant LANs which in turn might be connected to a pair of firewalls. The ERCOT-provided equipment connections also support a migration path from a non-redundant simple configuration to a robust LAN design without having to upgrade or replace ERCOT components.

During the equipment installation phase, ERCOT will work with the Participant to ensure that the Participant’s connections to the ERCOT switches meet the Participant’s requirements for reliability and performance. As changes occur on the Participant LAN that affect the ICCP data path, such as addresses, equipment features, or LAN technology, ERCOT will adjust the configuration parameters needed in the ERCOT-provided equipment.

# ICCP Connections

The protocol suite configured for the ERCOT ICCP network is OSI over TCP/IP using the Transport mapping layer specified in RFC 1006.  The complete profile for the ERCOT network is illustrated in Figure 3.3.

Figure 3.3 Network Protocol Suite

There will be variations at the physical layer (Layer 1) dependent on the Participant’s local communications architecture.  For example, the ICCP component of the EMS could be connected to the network router via other connection types such as any variation of Ethernet connections or a serial link such as an HSSI, RS-232, etc.

The dotted line represents the logical line of demarcation between Participant-provided equipment and ERCOT-provided equipment.  Participants establishing links will coordinate their configurations and schedules with ERCOT in preparation of link commissioning and testing.

## Establishing ICCP Associations

An ICCP Association is equivalent to a TCP connection.  ICCP Associations can be formed as “single-use” or “dual-use” Associations.  These Associations have to do with the client/server role taken by the Participant in its data exchange with ERCOT.  The Participant’s system acts as client when it receives data from ERCOT because of a request for the data.  The Participant’s EMS acts as a server when it sends data to ERCOT as requested.  A given ICCP node perceives its client and server roles to be separate and independent data exchange processes.  Environments exist where one side acts only as a client and the other acts only as a server, although this is unlikely to be the case for any ICCP node communicating with ERCOT.

A Single-use Association is one where one side of the Association always performs the client role and the other side performs the server role.  With Single-use Associations, two Associations are required in order for each side to act as both a client and a server.  With a Dual-use Association, one Association supports both ends acting as both client and server.  The concept is illustrated in Figure 3.4.

Figure 3.4 Types of Associations

ICCP vendors have taken different approaches to supporting Association use.  Some systems allow only one type while others allow both.  ERCOT supports both kinds of Associations in order to be compatible with any system.  However, to conserve resources and simplify system management, ERCOT requires Participants to establish Dual-use Associations if their ICCP nodes support it, even if they also support Single-use Associations.

The ICCP standard specifies that when Single-use Associations are established, the client always initiates the Association. For Dual-use Associations, the establishing side is determined by agreement.

ERCOT requires that ERCOT always establish Associations when a Dual-use Association is configured.

ERCOT is reconsidering this policy. The finalized policy will be included in the next NICD revision.

When Single-use Associations are implemented, ERCOT will establish the client-side Association with the Participant’s server function, and the Participant must establish the client-side Association with ERCOT’s server function in compliance with the ICCP standard.

Figure 3.5 and Figure 3.6 show how each conformance block operates over a set of Single-use Associations. The figures show that in all cases the client makes requests over the Association assigned to its client role, and receives data from the server over that same Association.  As the figures suggest, data exchange with ERCOT presently makes use of ICCP Conformance Blocks 1 and 2 only.

Figure 3.5: Single-use Association (ERCOT Server)

Figure 3.6: Single-use Association (Participant Server)

Note: At the present time, the ERCOT communication architecture is designed to provide generation control, including ancillary service dispatch, using the RTU interface. However, ICCP might be used to convey dispatch commands to relevant Participants in the future. Generation control via ICCP will only be considered after a firm determination has been made that ICCP can consistently meet the performance and reliability requirements of this critical function. It is anticipated that ICCP Conformance Block 6 (control commands) will be implemented to support any future use of ICCP for generation control.

## Association Restrictions (Peer Communication)

The network architecture establishes Permanent Virtual Circuits (PVCs) between each Participant and ERCOT.  Although it is theoretically possible for Participants to establish peer Associations with each other, all such traffic would pass through routers located at ERCOT.  The ERCOT routers are configured to accept only traffic that originates with a Participant and is destined to ERCOT. Therefore, peer communication between Participants is not allowed.

## Association Identifiers

Association identifiers follow the ERCOT standard format described in this section.

Table 3.2: AP Title Format

| Field Name | Format (or Value) | Description |
| --- | --- | --- |
| ISO Prefix | 0002 | A standard ISO AP Title designator for applications using MMS. It stands for (joint-iso-ccitt) |
| Naming Hierarchy | 0016 | A standard designator indicating that the AP Title follows the country-based naming hierarchy. |
| Org ID | 0001 | ERCOT’s Organization Identifier. |
| Participant ID | 00AA 00AA 00AA 00AA | The Participant’s ICCP identifier. This identifier is also used in Domain names and Bilateral Table Names. The assigned Participants’ ICCP identifiers are included on the Association Information Exchange Form (AIEF). |
| Node ID | 00AA | The text representation of an integer designating the node number of the Participant’s ICCP node. The primary control center ICCP node is typically node “1” and the backup is typically node “2”. |
| Application ID | 0073 | This value specifies that ICCP is the application in use on this Association. |

The format shown as 00AA is a sequence of four integers.  The first two integers are zeros, and the last two are the decimal representation of an ASCII character.  As an example of a valid AP Title, ERCOT’s primary control center ICCP node would specify an AP Title of:

0002 0016 0001 0065 0067 0077 0069 0049 0073

The Participant ID and Node ID fields above represent the text string ACME1.

This Association Identifier convention is compatible with the NERC standard for naming ICCP Associations. ERCOT is considering the use of alternate formats that conform to other standard naming hierarchies. The format described here in the next NICD revision will represent the preferred hierarchy and its naming convention.

## Protocol Selectors

Protocol selectors are numerical identifiers for the Presentation Selector, Session Selector, and Transport Selector.  They are specified as two 8-bit decimal integers of the form NN NN, as in 00 01.

Although most systems specify 00 01 for all protocol selectors, the values required are dependent on the ICCP vendor’s system.  ERCOT’s local ICCP implementation does not require protocol selectors to be unique between ICCP nodes.  Therefore, ERCOT can support any protocol selector identification scheme as required by the various Participant systems. As a result, Participants are free to specify the desired protocol selector values on the AIEF.

## TCP Port Number

ICCP uses the TCP port number 102.  This is the IETF officially assigned TCP port for all connections to a system implementing RFC1006. TCP Port 102 is the port number for the Transport Layer Service Access Point (TSAP) for Transport Class 0.

## System Connections

ERCOT operates the following systems:

- Primary ICCP Node at Taylor

- Backup ICCP Node at Austin

- Development System Node

The choice of network, circuit, and routers that traffic traverses is automatically determined by the routing protocols of the network redundancy architecture.  The intermediate system network elements operate under dynamic routing so that circuit failure recovery does not involve the end systems.  However, fixed IP addresses are assigned to each of ERCOT’s ICCP nodes. The IP addresses and AP Titles of the ERCOT ICCP nodes are provided on the AIEF. The Participant must respond to these addresses when processing Association Initiation requests.

In order to ensure that ERCOT establishes an Association with the correct Participant ICCP node, ERCOT will list IP addresses and AP Titles for participant nodes in the following order on the AIEF:

- The primary node at the primary operating facility

- The secondary node at the primary operating facility

- The primary node at the secondary operating facility

- The secondary node at the secondary operating facility

Finally, ERCOT will list an additional IP address for the Participant’s development/test ICCP node. This node will not be included in the search list for operational nodes. However, the development/test node address is included in the ERCOT directory to support testing exercises with Participants during their development phase or for problem resolution.

A development/test ICCP node address will be assigned to a Participant whether or not the Participant actually has such an ICCP node. The AIEF includes a field for the Participant to indicate whether such an ICCP node exists. If a Participant later acquires a development/test ICCP node, this is the address ERCOT will use to access the node.

ERCOT assigns these IP addresses to the Participant’s ICCP nodes recognizing that the Participant may implement Network Address Translation (NAT) in their firewalls/routers. Using NAT, the Participant can assign internal IP addresses to the ICCP nodes that are compatible with the Participant’s corporate LAN addressing plan. Participants are strongly encouraged to implement such an address translation scheme inside the line of demarcation. Participants choosing not to implement NAT may have to contend with IP address conflicts.

# ICCP Certification Testing

In order for a new Participant to join the ERCOT Network, a formal ICCP Certification Test must be performed.  This test has a two-fold purpose:

- It ensures that the new Participant’s equipment is properly configured and will not interfere with the communication functions being performed by other network Participants

- It provides basic interoperability testing to ensure that the standards specified by ERCOT are met.

The ERCOT ICCP Certification Test Plan is the document used for ICCP Certification testing. The document is available on the TexasChoiceProgram web site. The test plan is primarily designed to certify that the Participant’s ICCP nodes successfully interoperate with ERCOT’s ICCP nodes. Certification testing is not intended to be a comprehensive test of the Participant’s ICCP implementation. Therefore, the ERCOT ICCP Certification Test Plan should not be used as a means for performing an Acceptance Test of the vendor’s ICCP product.

# ICCP Protocol

The ICCP documents listed in Section 1.2 refer to the ICCP protocol standard and the ICCP User's Guide. These documents provide a comprehensive definition of the ICCP protocol. Be aware that those documents are oriented toward ICCP protocol developers. Nevertheless, interested readers are encouraged to review the standard since an understanding of the ICCP architecture and terminology will facilitate communication with ICCP product vendors.

## Supported Features

During Association establishment, the client accesses the ICCP standard object named Supported_Features.  This object returns a bit string that specifies the ICCP Conformance Blocks supported in the server.  All ICCP implementations shall provide the features listed in Table 5.3.

Table 5.3 Required ICCP Supported Features

| Conformance Block | Bit Position |
| --- | --- |
| Block 1 | 0 |
| Block 2 | 1 |

## ICCP Version

ICCP defines a variable called TASE2_Version.  A client reads this variable after an Association is established to determine that the protocol versions will interoperate.  The present value of TASE2_Version is:

MajorVersionNumber = 1996	MinorVersionNumber = 8

All systems shall conform to this ICCP version. The variable TASE2_Version is VMD-specific, meaning that it is a system-wide global value not associated with any particular Domain. TASE2_Version should be considered as a hard-coded value imbedded in the ICCP vendor’s product release as opposed to a configuration parameter.

## Bilateral Tables

Bilateral Tables reflect a security mechanism ICCP defines to control access to data objects.  A Bilateral Table is a computer-generated reflection of a Bilateral Agreement.  A Bilateral Agreement is a formal document stating the objects a data owner is willing to provide to a data user. Bilateral Agreements and Bilateral Tables provide for contractual agreements between data exchange partners.

In practical application, few electric utility organizations implement the full methodology suggested by the ICCP standard for Bilateral Agreements.  Such a formal, contractual process is unrealistic due to the long lead-times that would be needed to effect a change in the objects exchanged between companies.  Instead of engaging in continuously negotiated data exchange contracts, ISOs typically develop a data privacy policy defining the acceptable use and accessibility of a data owner’s objects.  This eliminates the need for a separate detailed Bilateral Agreement.  Consequently, the ICCP Bilateral Table implements access controls that reflect the data privacy policy.

### Bilateral Table Names

Various ICCP designs take different approaches to implementing Bilateral Tables.  Most systems do not implement a particular Bilateral Table data structure.  Rather, the definition of data objects includes access control attributes and the objects are assigned to Domains. Access control attributes combined with Domain assignment implement the concept of the Bilateral Table.  Regardless of the specific internal implementation, ICCP exposes a Bilateral Table identifier designed to ensure that the data object access list between ERCOT and a particular Participant is consistent. In the ICCP standard, this identifier is called the Bilateral Table Version. However, this NICD refers to the ICCP Bilateral Table Version as the Bilateral Table Name.

The ERCOT naming standard for the Bilateral Table Name includes a text identifier and version number. The number portion of the Bilateral Table Name is typically incremented each time the Bilateral Agreement changes.  In the ERCOT system, the Bilateral Table version number will rarely change.

Bilateral Table Name mismatches result in a failure to establish an Association.  Furthermore, Bilateral Table Name changes require Associations to be restarted.  ERCOT requires that Associations always function when physically possible. No procedure should be defined that would artificially cause an Association to fail.  The following Bilateral Table version management procedure is designed to be consistent with this policy.

### Bilateral Table Version Management

Bilateral Table Names have the form:

ERCT_pppp_nnnn

Where:

pppp is the company identifier for the Participant

nnnn is the Bilateral Table version number

The following example specifies a Bilateral Table Name for an Association between ERCOT and Acme:

ERCT_ACME_0001.

The initial Bilateral Table Name is specified on the AIEF. There shall be only one Bilateral Table Name related to an Association between ERCOT and a given Participant. Specifically, the data object access list that ERCOT’s ICCP server provides to the Participant is identified under the same Bilateral Table Name as the data object access list that the Participant’s ICCP server provides to ERCOT. Once the Bilateral Table Name is defined, only the version number will subsequently change.

In order to facilitate frequent and rapid changes to the Bilateral Table, the Bilateral Table version number will change infrequently.  Simply adding or deleting objects from a Participant’s Domain does not require a change to the Bilateral Table version.

The first Bilateral Table version shall always be 0001.  This version number will not change without the agreement of ERCOT.  Any change to the version number must be performed as part of a test similar to, though not as extensive as, the ICCP Certification test referred to in Section 4.  The version number should only be changed when the data object list is modified so extensively that ERCOT and the Participant agree that it is in the best interest of both parties to re-synchronize the Bilateral Table.

The effect of this policy is to ensure that Associations can be established even if the Bilateral Table between the client and server disagree.  In this situation, when the client requests an object which it can no longer access, an object access error will be reported. The client can then simply remove the object’s definition either programmatically or by human intervention.

It is also possible that new items will be made available in the server of which the client is not aware.  To avoid this problem, the client can periodically retrieve the names of all the objects in the server to which the client has access.  The client can then compare this list with the objects defined in its database.  If any missing objects are discovered, and deemed by the client to be important, the client can add the objects to the database.

Be aware that whether or not a tool is available from the vendor to access the data object list, most changes are implemented as part of power system modeling. Updating the model involves a formalized exchange of model information between ERCOT and the Participant. There may be some exceptions where data not related to the model is exchanged, but any database changes important to the client will usually be conveyed by the people involved in making the changes.

## ICCP Conformance Blocks

This section describes the ICCP Conformance Blocks required to support the exchange of data between ERCOT and its Participants. The required ICCP Conformance Blocks are:

- Block 1 – Basic services including transfer of real-time data periodically.

- Block 2 – Transfer of real-time data by exception.

ICCP Conformance Blocks 1 and 2 are used to exchange real-time information about data elements. These data elements typically correspond to points in an EMS or SCADA system.  In ICCP-speak these points are called Data Value Objects.  Block 1 functionality is limited to direct value reads and periodic value reporting.  Block 2 adds reporting by exception and a variety of report generating triggers. Block 2 provides the most efficient mechanisms for real-time data exchange.

Although a client can read individual Data Value Objects, the greatest flexibility results from organizing points into Data Sets.  Data sets are lists of Data Value Objects. Each Data Value Object referenced in a Data Set can be of any data type.

A Transfer Set is a data structure that specifies the conditions under which the server should send the content of a Data Set to the client. Transfer Set parameters are specified by the client. Parameters include such things as a reference to a Data Set (what is to be transferred), the conditions of transfer (when data should be transferred), and any limitations on the data report (such as RBE). After setting the Transfer Set parameters, the client creates the Transfer Set in the server, then starts the Transfer Set.

Transfer Set parameters and ERCOT usage standards are described in more detail in Section 5.9.

## ERCOT MMS PDU Size

ERCOT networking using ICCP shall support a maximum MMS PDU size of 32000 bytes. ICCP negotiates the actual maximum MMS PDU size during connection establishment.

## Domain Naming Standard

Every ICCP server shall implement Domains.  These are conceptual containers for data to be exchanged between a particular client and server.  Domains are server specific. That is, a Domain is configured in a server to contain the values a particular client can access. The client must then know the name of the Domain in the server to which it has access in order to access those values. ERCOT implements a Domain for each Participant, and requires that each Participant acting as a server implement a Domain for ERCOT.

Domain names have the form:

ssss_cccc_tttt

Where:

ssss is the company identifier for the server

cccc is the company identifier for the client

tttt identifies the type of Participant

Values for tttt are assigned by ERCOT to each Participant.  Examples of these modifiers are:

QSE identifies a Qualified Scheduling Entity

TDSP identifies a transmission owner company

REP identifies an agent such as an aggregator

For example, here is the Domain name for the client/server Association where the server is ERCOT and the client is Acme Transmission services:

ERCT_ACME_TDSP

ERCOT stores the values accessible to Acme in this Domain. Acme then includes this name in its access requests. Conversely, Acme’s system, when acting as a server would contain a Domain for ERCOT configured as:

ACME_ERCT_TDSP

ERCOT then uses this name when accessing data from the Acme ICCP server.

ICCP vendors design their Domain architectures in various ways because the ICCP standard does not impose any specific design requirements on Domain implementation. Domain implementation in the ICCP server is usually straightforward, since a storage area for each ICCP client is obviously needed to segregate the values for one client from those for other clients. Each of these storage areas is distinguished by the Domain name.

An ICCP client does not require a separate storage area to contain the values accessed from individual servers. It is only required that the client provide the correct Domain name when an access request is made. However, most ICCP vendors do set aside separate storage areas in the client so that a named Data Value Object accessed from one server won’t override the same object name accessed from another server. Because of this artifact of implementation, vendors sometimes adopt the terminology of a “remote” Domain versus a “local” Domain. Unfortunately, the meaning of “remote” versus “local” is nonstandard, so it may have the opposite meaning between different vendors.

Under the assumption that “local” means “in the server”, vendor documentation often speaks of creating a “remote” Domain and a “local” Domain having the same name. For example, a vendor might include in its ICCP configuration documentation, instructions to create a local Domain with the name ACME_ERCT_TDSP in Acme’s ICCP node. The documentation might also refer to the creation of a remote Domain with the same name in another ICCP node, such as ERCOT’s node. The local Domain simply means that the user is configuring a storage area in its server that will contain the values to be retrieved by the client node (ERCOT), which will refer to the name ACME_ERCT_TDSP.

The vendor may then discuss creating a remote Domain named ERCT_ACME_TDSP in the Acme node. In this case the Acme node, acting as a client, will retrieve data objects from the Domain named ERCT_ACME_TDSP in the ERCOT node which is acting as a server. These values will then be stored in a named region being set aside for that purpose.

The fact that vendors use the non-standard terms “local” and “remote”, and assign arbitrary meanings to the terms, is more confusing than helpful. The ICCP standard does assign well-defined meanings to the terms “client” and “server” and describes ICCP operations in those terms. Specifically, a “server” makes values available to interconnected computers, and a “client”, requests the available values. Servers define (and create) Domains, and clients refer to them when requesting data. The illustration given in Exhibit 5.1 describes the intent of the standard and the effect of its interpretation by the product vendors.

Exhibit 5.1 Domain Names and Their Implementation

Domain names are exchanged on the AIEF. ERCOT will assign Domain names consistent with the naming standard specified here. The above discussion of Domains is given to avoid confusion about the information on the AIEF. The point here is that a Domain is always a server specification. Domains are never assigned to client nodes.

## Data Set Naming Standard

Data Set names follow a convention similar to the Domain naming convention as follows:

Data Set identifiers have the form:

ssss_cccc_nnnn

Where:

ssss is the company identifier for the server

cccc is the company identifier for the client

nnnn is a sequence number that uniquely defines the Data Set

If ERCOT were to create five Data Sets in the Acme server, the Data Sets would have the following names:

ACME_ERCOT_0001

ACME_ERCOT_0002

ACME_ERCOT_0003

ACME_ERCOT_0004

ACME_ERCOT_0005

A similar set of data sets created in the ERCOT server by Acme would have the following names:

ERCOT_ACME_0001

ERCOT_ACME_0002

ERCOT_ACME_0003

ERCOT_ACME_0004

ERCOT_ACME_0005

Clients create Data Sets in the server, so it would seem unnecessary to include the name of the server since every data set in a given server would include the name of the server.  However, doing so facilitates identification of Data Set locations when printed reports from different systems are combined in a single document.

## ERCOT Defined ICCP Objects

### Data Object Naming Standard

The ERCOT standard for ICCP Object names is illustrated in the following name descriptor.

ccccrrrssssssssvvvveeeeeeeeffff

Where:

cccc	is the 4-character company name

rrr	is the 3-character equipment type descriptor

ssssssss	is the 8-character station name

vvvv	is the 4-digit voltage level. The last digit of this name field is to the right of an implied decimal point. For example, if the voltage level is 138KV, then the digits 1380 would be entered. If the voltage level is 13.8KV, then the digits would be 0138.

eeeeeeee	is the 8-character equipment name

ffff	is a 4-character units specification of the measured value

Each field in the name must be padded with underscores where necessary to meet the specified field component length.

The following Data Object name conforms to the ERCOT naming convention standard:

ACMEBS_BARTON__1380BA_138__KV__

### ERCOT ICCP Objects

Exhibit 5.2 lists the types of data objects exchanged with Participants, and the labeling standards for each.

Exhibit 5.2 ERCOT ICCP Data Object Definitions

| Equipment Type | Type Descriptor | Measurement | Unit | ICCP Data Type | Sign Convention | Object Name Example CCCCRRRSSSSSSSSVVVVEEEEEEEEFFFF |
| --- | --- | --- | --- | --- | --- | --- |
| Bus | BS | Voltage | KV | RealQTimeTag | Always positive | ACMEBS_EXASUB__3450BUS1A___KV__ |
|  |  | Frequency | HZ | RealQTimeTag |  | ACMEBS_EXASUB__3450BUS1A___KV__ |
| Transformer | XF | Megawatts | MW | RealQTimeTag | Positive = flow into transformer | ACMEXF_EXASUB__1380AUTO_1__MW__ |
|  |  | Megavars | MV | RealQTimeTag |  | ACMEXF_EXASUB__1380AUTO_1__TAP_ |
|  |  | Tap Position | TAP | RealQTimeTag |  | ACMEXF_EXASUB__1380AUTO_1__TAP_ |
|  |  | Status | ST | StateQTimeTag |  | ACMEXF_EXASUB__1380AUTO_1__ST__ |
| Line | LN | Megawatts | MW | RealQTimeTag | Positive = flow out of substation | ACMELN_EXASUB__0690SBA_SBB1MW__ |
|  |  | Megavars | MV | RealQTimeTag |  | ACMELN_EXASUB__0690SBA_SBB1MV__ |
|  |  | Status | ST | StateQTimeTag |  | ACMELN_EXASUB__0690SBA_SBB1ST__ |
| Shunt | SH | Megavars | MV | RealQTimeTag | Positive = supplying vars | ACMESH_EXASUB__1380SHU_1___MV__ |
|  |  | Status | ST | StateQTimeTag |  | ACMESH_EXASUB__1380SHU_1___ST__ |
| Circuit Breaker | CB | Megawatts | MW | RealQTimeTag | Positive = flow out of bus section into equipment | ACMECB_EXASUB2_3450OCB_3580MW__ |
|  |  | Megavars | MV | RealQTimeTag |  | ACMECB_EXASUB2_3450OCB_3580MV__ |
|  |  | Status | ST | StateQTimeTag |  | ACMECB_EXASUB2_3450OCB_3580ST__ |
| Load | LD | Megawatts | MW | RealQTimeTag | Always negative | ACMELD_EXASUB1_0690XLD_1___MW__ |
|  |  | Megavars | MV | RealQTimeTag |  | ACMELD_EXASUB1_0690XLD_1___MV__ |
| DC Injection | DC | Megawats | MW | RealQTimeTag | Positive = flow out of substation | ACMEDC_DCTM_E__3450DC_1____MW__ |
|  |  | Status | ST | StateQTimeTag |  | ACMEDC_DCTM_E__3450DC_1____ST__ |

## Transfer Set Definition Standards

There are three types of Transfer Sets within ICCP. Data exchange in the ERCOT system requires only the Data Set Transfer Set.

A Transfer Set specifies the conditions under which a referenced Data Set is to be transferred from the server to the client. As a minimum, the Participant’s server shall support the following Transfer Set transmission parameters:

Start Time	Defines the time that the server is to begin monitoring conditions that will trigger a Data Set Information Report to be sent to the client.  In addition to a valid time value, a time value of zero shall be supported

Interval	Defines the frequency at which a periodic Data Set Information Report will be sent to the client.  This value shall be ignored unless Interval Timeout is specified as a Transmission Condition.  Limitations on the value of Interval can be found in the Workbook.

Buffer Time	Defines the amount of time the server will wait after an object changes before generating the Data Set Information Report.  Buffer Time is applicable only to the Object Change Transmission Condition.

Integrity Check	Defines the frequency at which all of the objects in the Data Set will be sent to the client.  Integrity Check is applicable only if RBE is specified.  Limitations on the value of Integrity Check are the same as those for Interval and can be found in the Workbook.

RBE	Specifies whether the Data Set Information Report will contain all the objects in the Data Set or only the objects which have changed since the last Data Set Information Report.

The Transfer Set also includes a parameter that specifies the Transmission Condition.  That is, the condition(s) that the server must monitor once Start Time arrives.  As a minimum, the Participant’s server shall support the following Transmission Conditions:

Interval Timeout	This condition specifies that a Data Set Information Report shall be sent to the client each time Interval expires.

Object Change	This condition specifies that a Data Set Information Report shall be sent to the client whenever any object in the Data Set changes.

Integrity Timeout	This condition specifies that the entire Data Set is to be sent to the client in a Data Set Information Report whenever Integrity Check expires.

In the ERCOT Network, Data Sets and Transfer Sets are used to organize data into different timing groups and exception reporting groups.  Since most of the data transfers across an Association are from the Participant’s ICCP node acting as a server, the organization and timing is largely invisible to the Participant.

In its ICCP server role, ERCOT will be processing data requests from many Participants. In order to minimize the performance impact on the ERCOT system, Participants shall adhere to the following Transfer Set and Data Set limitations:

- Status data shall always be acquired using Report by Exception. The Integrity Interval shall not be less than 30 minutes.

- Values representing analog measurements and counters shall be acquired at an interval of not less than 30 seconds.

- Data Sets shall not contain mixed data types that would cause a conflict in the Transfer Set limitations specified in 1) and above. More specifically, Data Sets containing analog measurements and counters shall not also contain status values unless the status values therein are a direct component of the measurements or counters.

Some of the required data exchange transactions specified in Attachment A, ERCOT Data Exchange Requirements, found in Communicating with ERCOT, exceed the restrictions given here. The timing specifications in the ERCOT Data Exchange Requirements table take precedence over these limitations. However, only the transactions defined in that table are allowed to exceed these limitations.

## Data Quality

Each Participant shall determine and maintain proper quality indicators for all data being transmitted to ERCOT.  Participants shall report the source, quality, and normality of each value transmitted to ERCOT.

Point failures are generally due to hardware malfunctions or maintenance procedures.  Any value calculated using a failed point must also be reported as a failed value.  For example, if a point representing the output of an on-line generator has failed, the total generation for that company or generation facility must also be reported as a failed quantity.

The last good value for any failed point is the value sent to ERCOT.  When a point fails for an extended period, a manual update of the point’s value is necessary once every 30 minutes to keep the data as accurate as possible.

ICCP provides the following categories of data quality:

- Validity

- Current Source

- Normal Source

- Normal Value

The quality definitions in each category are defined by ERCOT according to the following tables.

Table 5.4 Validity Quality Code Definitions

| Validity Flag Name | Definition |
| --- | --- |
| VALID | The data value is valid. |
| HELD | The data value is the last good value sent to ERCOT. The point has been manually taken off scan. |
| SUSPECT | The data value is the last good value sent to ERCOT. Point telemetry has failed at the source. |
| NOTVALID | The data value is the last good value sent to ERCOT. The last telemetered receipt of the value at the source exceeded the point’s reasonability limits. |

Table 5.5 Current Source Quality Code Definitions

| Validity Flag Name | Definition |
| --- | --- |
| TELEMETERED | The data value was received from a telemetered source. |
| CALCULATED | The data value was calculated based on other data values. |
| ENTERED | The data value was entered manually. |
| ESTIMATED | The data value was estimated. (State Estimator, etc.) |

Table 5.6 Normal Source Quality Code Definitions

| Validity Flag Name | Definition |
| --- | --- |
| TELEMETERED | The data value is normally received from a telemetered source. |
| CALCULATED | The data value is normally calculated based on other data values. |
| ENTERED | The data value is normally entered manually. |
| ESTIMATED | The data value is normally estimated. (State Estimator, etc.) |

Table 5.7 Normal Value Quality Code Definitions

| Validity Flag Name | Definition |
| --- | --- |
| NORMAL | The point value is that which has been configured as normal for the point. |
| ABNORMAL | The point value is not that which has been configured as normal for the point. |

# Real-Time Data Semantics

In order to assure full interoperability between ERCOT and its Participants, certain data values must have common semantics.  These semantics are defined in this section.  Each Participant’s system shall provide the required data conversion functions to ensure that values are sent to ERCOT with the meanings defined here.

## Status Values

The convention for status values shall be as defined in Table 6.8.

Table 6.8 Status Value Semantics

| 00 | 01 | 10 | 11 | Device |
| --- | --- | --- | --- | --- |
| Between | Tripped | Closed | Invalid | Recloser |
| Between | Off | On | Invalid | Recloser |
| Invalid | Off | On | Invalid | Breaker |
| Invalid | Open | Closed | Invalid | Breaker |
| Invalid | Auto | Manual | Invalid | Any |
| Invalid | Normal | Alarm | Invalid | Any |
| Invalid | Local | Remote | Invalid | Any |
| Invalid | Raise | Lower | Invalid | Transformer |
| Invalid | Not Ready | Ready | Invalid | Any |
| Invalid | Off Line | Available | Invalid | Any |

## Energy and Reactance Values

Values representing energy and reactance are to be provided in the units defined in Table 6.9.

Table 6.9 Energy and Reactance Values

| Value Semantics | Unit of Measure |
| --- | --- |
| Power | Megawatts (MW) |
| Energy | Megawatt-hours (MWh) |
| Reactance | Megavar (MVAR) |
| Loss | Megawatt-hour (MWh) |
| Frequency | Cycles per Second (Hz) |
| Voltage | Kilovolts (kV) |
| Penalty Factor | Actual factor value |

For information such as schedules, forecasts, and other similar data, ERCOT provides the Portal and API (Programmatic Interface [PI]) interfaces. Refer to the guides for these interfaces as well as the ERCOT XML specifications for more information.

This note has been included to assist the Participant’s ICCP procurement planning. Participants installing RTUs for energy dispatch and/or ancillary service functions will not be required to switch to ICCP as the primary means for performing such control operations.

TCP does not communicate with ICCP. Rather, it communicates with the ISO Transport service. The higher layers of the protocol stack then identify ICCP by the AP Title described in Section 3.3.

In order to ensure the best possible performance from the ERCOT Private Network, ERCOT has designed an IP addressing plan supporting efficient routing updates. Specifically, ERCOT makes extensive use of subnetting to minimize traffic generated by the routing protocols (routing table updates). Participants also need the flexibility to implement their own addressing plans for the same reason. Implementing NAT allows both organizations to meet their performance requirements with a minimum of conflicts.

This is the function of the ICCP service called GetDataValueNames. The availability of a tool to access the data object list is product dependent. Participant’s should ask their vendors if such a tool is available.

This naming convention for Data Sets is a recommendation only.  Some implementations create Data Set names internally so that the user has no control over their form.  For those systems where the user can assign Data Set names, the convention specified here is the preferred form.