Combined Cycle Power Plant Data Request

Request for Combined Cycle Power Plant Modeling Data

Please provide the following Key Parameters:

| Key Parameter | Value(s) |
| --- | --- |
| Gas turbines(s) nominal rating(s) (ISO conditions) |  |
| Gas turbines(s) base load power output under summer conditions |  |
| Gas turbines(s) peak load power output under summer conditions (if applicable) |  |
| Gas turbines(s) base load power output under winter conditions |  |
| Gas turbines(s) peak load power output under winter conditions (if applicable) |  |
| Steady state droop for gas turbine(s) speed control |  |
| MW base for droop |  |
| Number of GTs connected to a common HRSG |  |
| Number of stages in the steam turbine |  |
| Steam turbine(s) nominal ratings(s) and any seasonal variations |  |
| Typical split (in terms of MW) of the available steam between electrical power production and co-generation usage, if applicable |  |
| Typical secondary steam input to the Steam unit (in terms of MW) for electrical power production, if applicable |  |

Please provide the arrangement of the HRSG and a brief description of the steam path/steam cycle (number of GTs connected to a common HRSG, number of stages in the steam turbine, steam usage in co-generation arrangement, etc).

Please provide the arrangement of the substation, including generator step-up transformer(s), and auxiliary load(s) transformer(s).

Excel Dispatch Spreadsheet

The Excel Dispatch Spreadsheet contains the information for one combined cycle train, i.e., the dispatch of the gas and steam turbines that are effectively linked through a common HRSG.  (If the plant has two separate trains of combined cycle units, the dispatch information should be split into two Excel files).

Each file contains three worksheets: bus, dispatch_summer, and dispatch_winter.  The tab bus contains the bus number and machine ID used for ERCOT’s planning cases for each generator, as well as the identification of the type of turbine (GT or ST).  The tab dispatch_summer contains the dispatch of the CCPP for summer conditions (high ambient temperature), while the tab dispatch_winter contains the dispatch for winter.

Please use the TestDispatch.xls spreadsheet as a template.

In the bus table, please enter the bus number, machine ID, unit name, and type (GT or ST) for each unit in the combined cycle train.

In the dispatch_summer table, please enter several representative dispatches of the units in the CC train.  Please provide the minimum dispatch on the gas turbines before the steam turbine can produce power.  Please also include those dispatch scenarios where some units are off.  Please include the full power output for the summer season (high ambient temperature).  Enter the auxiliary load in MW as Gross Gen minus Net Gen, for each dispatch.

In the dispatch_winter table, please enter representative winter dispatches, similar to the summer, except using winter ambient temperatures.

Below is an example of a dispatch table.

|  | U1 | U2 | U3 | U4 |  |
| --- | --- | --- | --- | --- | --- |
| SUMMER | Gross MW | Gross MW | Gross MW | Gross MW | AUX Load |
| Dispatch-1 | 52 | 0 | 0 | 0 | 6 |
| Dispatch-2 | 160 | 0 | 0 | 0 | 6 |
| Dispatch-3 | 0 | 160 | 0 | 0 | 6 |
| Dispatch-4 | 0 | 0 | 160 | 0 | 6 |
| Dispatch-5 | 160 | 0 | 0 | 20 | 7 |
| Dispatch-6 | 0 | 160 | 0 | 20 | 7 |
| Dispatch-7 | 0 | 0 | 160 | 20 | 7 |
| Dispatch-8 | 160 | 160 | 0 | 41 | 21 |
| Dispatch-9 | 0 | 160 | 160 | 41 | 15 |
| Dispatch-10 | 160 | 0 | 160 | 41 | 15 |
| Dispatch-11 | 160 | 160 | 160 | 87 | 21 |

Note that Dispatch-1 shows the minimum dispatch on the gas turbines (52 MW) before the steam turbine can produce steam.

Dispatch-11 shows the full power output for the summer.

If a plant has more than two seasonal dispatch tables, feel free to insert additional worksheets.

Gas Turbine – UCGBT model

UCGBT is a generic gas turbine model as developed by CIGRE.  This model is characterized by three major control loops:

- speed/load governor control (PID control with parameters Kpg, Kig and Kdg);

- acceleration control (PI control with parameters Kpa and Kia and acceleration limit setpoint aset);

- exhaust temperature control (PI control with parameters Kpt and Kit, with temperature limit setpoint Tlimit).

A reset controller (PI control with parameters Kmwp and Kmwi) can be used to represent an outer-loop control to maintain the units output at a pre-specified MW setpoint given by the plant operator.

The definition of the turbine rating is critical not only for the gas turbine parameters but also for the HRSG model.

The temperature limit should dictate the maximum power output of the turbine.  At maximum power output, the fuel demand is determined by the temperature control loop and the turbine is not responsive in case of disturbances resulting in frequency drop.  The unit is not capable of further increasing its power output, as would be requested by the speed governor control.  Events resulting in a frequency increase would result in a power output reduction, bringing the unit out of the temperature control and back into speed governor control.

Typical UCGBT Model Parameters

| CON | Value | Description |
| --- | --- | --- |
| J | 0.05 | Rp (s) Electrical power feedback droop |
| J+1 | 5.0 | Tp (p.u.) Electrical power feedback time constant (>0) |
| J+2 | 0.0 | Rv (p.u.) Governor feedback droop |
| J+3 | 0.0 | Kmwp (p.u.) Proportional gain for outer loop MW control |
| J+4 | 0.0 | Kmwi (s) Integral gain for outer loop MW control |
| J+5 | 0.0 | rfmax (p.u.) Maximum limit on outer loop MW control loop |
| J+6 | 0.0 | rfmin (p.u.) Minimum limit on outer loop MW control loop |
| J+7 | 0.0003 | dbd (p.u.) Intentional deadband |
| J+8 | 0.005 | err (p.u.) Intentional error limit |
| J+9 | 0.10 | Ta (>0) (p.u.) Acceleration control time constant |
| J+10 | 0.01 | aset (p.u.) Acceleration limit setpoint (see note 2) |
| J+11 | 15.0 | Kpg (>0) Speed governor proportional gain (p.u.) |
| J+12 | 3.0 | Kig (>0) Speed governor integral gain (p.u.) |
| J+13 | 4.0 | Kdg (p.u.) Speed governor derivative gain |
| J+14 | 0.05 | Tdg (p.u.) Speed governor derivative time constant |
| J+15 | 0.0 | Kpa (>0) Acceleration control proportional gain (p.u.) |
| J+16 | 10.0 | Kia (p.u.) Acceleration control integral gain |
| J+17 | 1.0 | Kpt (p.u.) Temperature control proportional gain |
| J+18 | 0.20 | Kit (p.u.) Temperature control integral gain |
| J+19 | 1.0 | Fmax (p.u.) Maximum fuel flow command |
| J+20 | 0.15 | Fmin (p.u.) Minimum fuel flow command |
| J+21 | 0.917 | Tlimit (p.u.) Temperature limit (see note 4) |
| J+22 | 2.50 | Tthcp (p.u.) Thermocouple time constant |
| J+23 | 10.0 | Tn (p.u.) Heat transfer lead time constant |
| J+24 | 15.0 | Td (p.u.) Heat transfer lag time constant |
| J+25 | 0.50 | Tv (>0) (p.u.) Fuel system time constant |
| J+26 | 1.00 | Vmax (p.u.) Maximum valve opening |
| J+27 | 0.0 | Vmin (p.u.) Minimum valve opening |
| J+28 | 1.0 | Fm (p.u.) Fuel flow multiplier (see note 2) |
| J+29 | 0.25 | Wf0 (p.u.) Full-speed no-load fuel flow |
| J+30 | 1.50 | Kt (>0) (p.u.) Turbine gain |
| J+31 | 1.00 | Ttn1 (p.u.) Turbine numerator time constant 1 |
| J+32 | 0.0 | Ttn2 (p.u.) Turbine numerator time constant 2 |
| J+33 | 1.5 | Ttd1 (p.u.) Turbine denominator time constant 1 |
| J+34 | 0.50 | Ttd2 (>0) (p.u.) Turbine denominator time constant 2 |
| J+35 | 0.95 | x1 – 1st point of turbine characteristic curve |
| J+36 | 0.95575 | F(x1) |
| J+37 | 1.00 | x2 – 2nd point |
| J+38 | 1.0010 | F(x2) |
| J+39 | 1.05 | x3 – 3rd point |
| J+40 | 0.97568 | F(x3) |
| J+41 | 180.0 | Trate – turbine rating (MW) (see note 1) |

notes:

1) User input. Model adopts generator MVA base as turbine rating if parameter TRATE = 0.0

2) the parameter CON(J+10) = aset should be set to +99 to disregard the acceleration limit control

loop

3) the CIGRÉ document suggests implementing F(x) as a look-up table or a piecewise linear

function, that would require specific manufacturer’s data to be defined. The present

implementation of this model assumes a quadratic approximation of the characteristics similar to

the one given in Figure C-1 of the CIGRÉ document. The user should enter three points [xi, F(xi)]

of the turbine characteristics curve and the model will determine the coefficients of a quadratic

equation given as F(x)= A x2 + B x + C. The characteristic in Figure C-1 can be approximated by

using the following points: [0.95, 0.95575], [1.0, 1.001], and [1.05, 0.97568].

4) Tlimit corresponds to fuel demand required for 1 p.u. turbine power i.e. = (1/Kt+Wfo).

Conversely, Tlimit determines the (steady state) maximum power output of the turbine:

Pmax = (Tlimit – Wf0 ) x Kt, expressed in per unit of turbine rating Trate.

5) This model was proposed in CIGRÉ Technical Brochure on Modeling of Gas Turbines and Steam

Turbines in Combined-Cycle Power Plants, Task Force 25 of Advisory Group 02 of Study

Committee 38, April 2003.

Heat Recovery Steam Turbine – UHRSG model

The generic heat recovery steam turbine model UHRSG represents an HRSG supplied by gas turbine exhaust heat output and supplying steam to a steam turbine.  It incorporates a simplified representation of the steam system, consisting of a single drum and a single turbine admission valve.

The model allows the representation of up to six gas turbines connected to a common heat recovery steam generator (HRSG).  The total power output of the gas turbines is related to heat through a look-up table (piece-wise linear) and the steam production is proportional to the heat provided by the gas turbines and the heat from supplementary firing, if any, represented by a constant heat input Qs.

The PGt points in the look-up table, associated with the parameters CON(J) through CON(J+13) in the model datasheet, should be provided in per unit of the total rating of the gas turbines connected to the HRSG, while the QG values are given in the rating of the steam turbine.  In other words, the base quantities for pressure, heat and steam flow are such that they are at 1.0 per unit when the mechanical power output of the steam turbine is 1.0 per unit of turbine rating.

The changes in drum pressure are characterized by a single time constant, usually in the range of a few minutes.  The typical value of 300 seconds is suggested in the CIGRE document for this parameter.

At initialization, if the turbine inlet pressure Pt is smaller than the minimum steam pressure Pref, then Pt is set to Pref and the valve position is calculated accordingly.  In this case, the turbine is operated under pressure control rather than sliding pressure mode.

The parameter Bv represents a by-pass valve and can be set to a constant value (between 0 and 1) to simulate a constant extraction of the steam coming from the boiler and thus reducing the power output of the steam turbine.  Setting Bv to zero means that no steam by-pass is present and thus all the available steam is used for electrical power production.  Setting Bv to 1.0 corresponds to bypass valve fully open and it reduces the steam pressure and/or the mechanical power output of the steam turbine.

This is a simplification of the actual steam process where the extraction might occur at multiple stages and/or pressure levels.  The by-pass valve does not represent the use of the low-pressure steam out of the turbine, but rather the by-pass of the steam turbine resulting in a reduction in generated electrical power.

The model has provision for additional over-frequency and under-frequency controls.  These controls might be required for simulations resulting in severe frequency excursions.

Typical UHRSG Model Parameters

| ICON | Value | DESCRIPTION |
| --- | --- | --- |
| M | 100 | bus number for gas turbine #1 |
| M+1 | ‘1’ | machine ID for gas turbine #1 |
| M+2 | 101 | bus number for gas turbine #2 |
| M+3 | ‘1’ | machine ID for gas turbine #2 |
| M+4 | 102 | bus number for gas turbine #3 |
| M+5 | ‘1’ | machine ID for gas turbine #3 |
| M+6 | 103 | bus number for gas turbine #4 |
| M+7 | ‘1’ | machine ID for gas turbine #4 |
| M+8 | 0 | bus number for gas turbine #5 |
| M+9 | ‘ ’ | machine ID for gas turbine #5 |
| M+10 | 0 | bus number for gas turbine #6 |
| M+11 | ‘ ‘ | machine ID for gas turbine #6 |

| CON | Value | Description |
| --- | --- | --- |
| J | 0.10 | Pgt1 (p.u.) – point 1 |
| J+1 | 0.0 | Qg1 (p.u.) |
| J+2 | 1.00 | Pgt2 (p.u.) – point 2 |
| J+3 | 1.00 | Qg2 (p.u.) |
| J+4 | 1.20 | Pgt3 (p.u.) – point 3 |
| J+5 | 1.00 | Qg3 (p.u.) |
| J+6 | 0.0 | Pgt4 (p.u.) –point 4 |
| J+7 | 0.0 | Qg4 (p.u.) |
| J+8 | 0.0 | Pgt5 (p.u.) – point 5 |
| J+9 | 0.0 | Qg5 (p.u.) |
| J+10 | 0.0 | Pgt6 (p.u.) – point 6 |
| J+11 | 0.0 | Qg6 (p.u.) |
| J+12 | 0.0 | Pgt7 (p.u.) – point 7 |
| J+13 | 0.0 | Qg7 (p.u.) |
| J+14 | 300.0 | Tdrum (>0) – Drum time constant (s) |
| J+15 | 0.15 | Km – Pressure loss due to flow friction in the boiler tubes (p.u.) |
| J+16 | 0.50 | Tv (>0) – Actuator time constant for main steam (p.u.) |
| J+17 | 10.0 | Kp – Pressure controller proportional gain (p.u.) |
| J+18 | 2.00 | Ki – Pressure controller integral gain (p.u./s) |
| J+19 | 3.00 | Tn –Turbine lead time constant (s) |
| J+20 | 10.0 | Td –Turbine lag time constant (s) |
| J+21 | 0.0 | Qs – heat from sSupplemental firing (p.u.) |
| J+22 | 0.0 | Bv –Bypass valve opening (p.u.) |
| J+23 | 0.50 | Pref – Minimum steam pressure reference (p.u.) |
| J+24 | 180.0 | Trate – Turbine rating (MW) |

Notes:

1) If less than six gas turbines are connected to this HRSG (M to M+11), bus number should be set

to 0 and ID should be set to ‘ ‘ (2 spaces between quotes). Machine ID should always be entered within

quotes (2 characters ID).

2) Any PSS™E turbine/speed governor model can be used in the gas turbines coupled to this model.

The UHRSG model will retrieve gas turbine rating from the following PSS™E models: GAST2A,

GASTWD, GGOV1, URGS3T, WSHYGP, WSHYDD and UCBGT. All other PSS™E models

will have gas turbine rating set to generator MVA base.

3) Points in the look-up table should have Qg greater or equal to zero and should monotonically

increase. Once a decrease is detected, no more points are considered in the look-up table. Thus,

the user can enter [0.0, 0.0] for those points not needed.

4) If less than 7 points are required in the look-up table (J to J+13), the remainder data points should

be set to [0.0, 0.0]. The heat Qg is considered constant and equal to the last value Qgi when Pgt is greater

than Pgti. Heat is not extrapolated beyond the last point in the look-up table.

5) The bypass valve opening Bv should be a number between 0 and 1. If a negative value is entered,

the model will calculate the bypass valve opening to minimize any imbalances in heat

6) Setting Bv to 0.0 corresponds to no steam bypass and all available steam is used for electric power

production

7) This model does not provide speed governor action (primary frequency control) in a stand-alone

mode, i.e., the speed governor control of the combined cycle power plant is done via the gas

turbines, with the steam turbine responding to the changes in power output of the gas turbines.

Therefore, this model cannot be used in the speed governor test activities GSTR/GRUN, where

each generator is considered in isolated operation. The model will maintain constant mechanical

power output if GSTR/GRUN is applied and thus frequency (speed) will ramp down at a constant

rate. These results should be simply discarded.

8) This model was proposed in CIGRÉ Technical Brochure on Modeling of Gas Turbines and Steam

Turbines in Combined-Cycle Power Plants, Task Force 25 of Advisory Group 02 of Study

Committee 38, April 2003.

9) Entries highlighted are user input.  Values shown are not default values.

Attachments:

TestDispatch.xls

UCBGT_datasheet.pdf

UHRSG_datasheet.pdf