| NOGRR Number | 110 | NOGRR Title | Synchronization with NPRR529, Congestion Management Plan |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Approved |
| Date of Decision |  | January 28, 2014 |  |  |
| Effective Date |  | February 1, 2014 |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Nodal Operating Guide Sections Requiring Revision |  | 2.5.1, Criteria for Removing Contingencies from the Reliability Unit Commitment Analyses 3.3.3, Resource Entity Responsibilities for Equipment Ratings (new) 3.7.2, Responsibility for Equipment Ratings 4.3.1, Remedial Action Plans (delete) 4.3.2, Real-Time and Short Term Planning 6.2.2, Design and Operating Requirements for ERCOT System Facilities 11, Constraint Management Plans and Special Protection Systems (new) 11.1, Introduction (new) 11.2, Special Protection System (new) 11.2.1, Reporting of SPS Operations (new) 11.3, Remedial Action Plan (new) 11.3.1, Remedial Action Plan Process (new) 11.4, Mitigation Plan (new) 11.5, Pre-contingency Action Plans (new) 11.5.1, Pre-Contingency Action Plan Process (new) 11.6, Temporary Outage Action Plan (new) |  |  |
| Protocol Sections Requiring Revision |  | 2.1, Definitions 2.2, Acronyms and Abbreviations 3.1.6.5, Evaluation of Proposed Resource Outage 3.10.7.4, Definition of Special Protection Systems and Remedial Action Plans 6.5.7.1.10, Network Security Analysis Processor and Security Violation Alarm |  |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) synchronizes the Nodal Operating Guide with revisions proposed by Nodal Protocol Revision Request (NPRR) 529 and also: - Moves language related to Special Protection Systems (SPSs) and Remedial Action Plans (RAPs) to new Section 11. - Formalizes two existing Constraint Management Plans (CMPs), Transmission Outage Action Plans (TOAPs) and Pre-Contingency Action Plans (PCAPs). - Eliminates the distinction between Type I and Type II SPSs. - Institutes a stakeholder comment process for RAPs that are proposed by Market Participants to provide for input from other Market Participants into ERCOT’s approval process for these Market Participant-proposed RAPs. |  |  |
| Reason for Revision |  | To provide clarity and transparency into existing activities. |  |  |
| Procedural History |  | - On 3/6/13, NOGRR110 and an Impact Analysis were posted. - On 4/8/13, Calpine comments were posted. - On 4/17/13, the Operations Working Group (OWG) considered NOGRR110. - On 5/15/13, ERCOT comments were posted. - On 5/15/13, OWG again considered NOGRR110. - On 6/17/13, CenterPoint Energy comments were posted. - On 6/19/13, OWG again considered NOGRR110. - On 6/27/13, Luminant Energy comments were posted. - On 6/27/13, OWG again considered NOGRR110. - On 7/11/13, a revised Impact Analysis was posted. - On 7/11/13, a second set of ERCOT comments were posted. - On 7/17/13, OWG considered the 6/27/13 OWG Report and Impact Analysis for NOGRR110. - On 8/2/13, a revised Impact Analysis was posted. - On 8/15/13, ROS considered NOGRR110. - On 9/9/13, Constraint Management Plan Revision Request Workshop comments were posted. - On 9/12/13, ROS again considered NOGRR110. - On 9/26/13, a revised Impact Analysis was posted. - On 10/3/13, TAC considered NOGRR110. - On 1/28/14, TAC again considered NOGRR110. |  |  |
| OWG Decision |  | On 4/17/13, OWG was in consensus to table NOGRR110 until after the May 6, 2013 NPRR528, NPRR529 & NOGRR110 Workshop. On 5/15/13, OWG was in consensus to table NOGRR110 for one month. On 6/19/13, OWG was in consensus to table NOGRR110 until the 6/27/13 OWG meeting. On 6/27/13, OWG was in consensus to recommend approval of NOGRR110 as amended by the 6/17/13 CenterPoint Energy comments and as revised by OWG. On 7/17/13, OWG was in consensus to endorse and forward the 6/27/13 OWG Report as amended by the 7/11/13 ERCOT comments and as revised by OWG, and the Impact Analysis for NOGRR110 to ROS. |  |  |
| Summary of OWG Discussion |  | On 4/17/13, participants discussed the order in which actions under a CMP will be implemented; whether the definitions proposed by NPRR529 align with NOGRR110; whether ERCOT should be required to issue a Market Notice any time a RAP is submitted; and the length of time an SPS is expected to remain in service after approval. It was requested that ERCOT schedule a workshop to discuss NPRR529, NOGRR110, and NPRR528, Clarification of Assessment of Chronic Congestion, to provide additional clarification. On 5/15/13, it was requested that NOGRR110 be tabled until the June 2013 OWG meeting to allow time for interested parties to review the 5/15/13 ERCOT comments. On 6/19/13, the 6/17/13 CenterPoint Energy comments were reviewed. There was a request for NOGRR110 to be tabled to allow time for additional review. On 6/27/13, the 6/17/13 CenterPoint Energy comments and 6/27/13 Luminant Energy comments were discussed. There was a request for the Resource Entity responsibilities related to equipment Ratings be addressed within a new Section 3.3.3 as Section 3.7.2 applies to Transmission Service Providers (TSPs); that “Congestion Management Plan” should be revised to “Constraint Management Plan” because CMPs may or may not apply to active congestion on the ERCOT System; that ERCOT should provide notification and post to the Market Information System (MIS) Secure Area any approval, amendment, or expiration of a CMP, where applicable; and that upon completion of ERCOT’s review of an SPS, ERCOT should provide all results and underlying studies to the SPS owner. ERCOT Staff stated that RAPs will be coordinated and approved by ERCOT and all RAP owners; and that ERCOT will employ CMPs to facilitate the market use of the ERCOT Transmission Grid while maintaining system security and reliability as required by Protocols and North American Electric Reliability Corporation (NERC) Reliability Standards. OWG requested that ROS grant NOGRR110 Urgent status for the purposes of keeping NOGRR110 on a similar timeline as related revision requests NPRR528, NPRR529, NPRR540, Clarification of Credible Single Contingency, NPRR541, SPS and RAP Modeling Clarification, NPRR542, Clarification of the Use of Emergency Condition, NOGRR109, Revisions to Definition of Credible Single Contingency for Operations Planning, NOGRR114, Synchronization with NPRR540, Clarification of Credible Single Contingency, and NOGRR116, Synchronization with NPRR542, Clarification of the Use of Emergency Condition. On 7/17/13, the revised Impact Analysis was discussed. Participants were concerned with limiting TOAP submissions to TSPs and suggested that any Market Participant should be allowed to submit a TOAP; that the use of CMPs could impact the market; and that TOs and Resource Entities should be included in the coordination of RAPs. ERCOT Staff clarified that impacts to non-TSP submitted TOAPs would be minimal if the status of the submitted TOAP was limited to communication with TSPs only. There was a request for the Steady State Working Group (SSWG), the Dynamics Working Group (DWG), and the System Protection Working Group (SPWG) to review paragraph (2)(g) of Section 11.2 and to provide comments if there are concerns with the proposed language. It was recommended that NOGRR110 be forwarded to ROS for review with a revised Impact Analysis. |  |  |
| ROS Decision |  | On 8/15/13, ROS unanimously voted to table NOGRR110. All Market Segments were present for the vote. On 9/12/13, ROS voted to recommend approval of NOGRR110 as amended by the 9/9/13 Constraint Management Plan Revision Request Workshop comments. There were two abstentions from the Independent Generator Market Segment. All Market Segments were present for the vote. |  |  |
| Summary of ROS Discussion |  | On 8/15/13, participants requested that NOGRR110 be tabled until after the 9/3/13 Constraint Management Plan Workshop where NOGRR110 and related revision requests NPRR528, NPRR529, NPRR540, NPRR541, NPRR542, NOGRR109, NOGRR114, and NOGRR116 will be discussed. On 9/12/13, it was noted that the Impact Analysis may be revised due to the 9/9/13 Constraint Management Plan Revision Request Workshop comments. |  |  |
| TAC Decision |  | On 10/3/13, TAC unanimously voted to table NOGRR110 until associated Constraint Management Plan NPRRs are approved. All Market Segments were present for the vote. On 1/28/14, TAC unanimously voted to approve NOGRR110 as recommended by ROS in the 9/12/13 ROS Report. All Market Segments were present for the vote. |  |  |
| Summary of TAC Discussion |  | On 10/3/13, there was no discussion. On 1/28/14, there was no discussion. |  |  |

| Business Case |  |  |
| --- | --- | --- |
| Business Case | 1 | - To provide additional clarity around current activities. |
|  | 2 | - The addition of a comment process for RAPs that are proposed by Market Participants should allow for improved transparency and help ensure that any RAPs that are approved through this process are non-discriminatory. |

| Sponsor |  |
| --- | --- |
| Name | Chad Thompson |
| E-mail Address | cthompson@ercot.com |
| Company | ERCOT |
| Phone Number | (512) 248-6508 |
| Cell Number |  |
| Market Segment | Not applicable. |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Kelly P. Landry |
| E-Mail Address | klandry@ercot.com |
| Phone Number | (512) 248-4630 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| Calpine 040813 | Proposed revisions to remove a duplicate reporting requirement related to SPS operations, to revise the acronym of Transmission Operator (TO) to “TOP,” and to allow Resource Entities to submit requests for Mitigation Plans, and requested examples of SPS and RAP designs, with focus on what differentiates them from each other. |
| ERCOT 051513 | Proposed revisions based on the discussion at the May 6, 2013 ERCOT NPRR528, NPRR529, and NOGRR110 Workshop. |
| CenterPoint Energy 061713 | Proposed revisions that would allow post contingency flows below the Emergency Rating to avoid unnecessary Load shed, make ERCOT responsible for SPS equipment owned by Generation Resources, and require ERCOT to issue Market Notice for new or modified CMPs. |
| Luminant Energy 062713 | Proposed revisions to allow more efficient use of CMPs and proposed to distinguish Mitigation Plans from other CMPs. |
| ERCOT 071113 | Proposed revisions to reduce risk of providing discriminatory access to information; remove a duplicative posting requirement; and make non-substantive administrative edits. |
| Constraint Management Plan Revision Request Workshop 090913 | Endorsed NOGRR110 as revised by the workshop. |

Comments

Please note that the baseline Operating Guide language in Section 6.2.2 has been updated due to the incorporation of NOGRR107, Disturbance Monitoring Requirements Clarifications, into the June 1, 2013 Nodal Operating Guides.

Please also note that NOGRR114, Synchronization with NPRR540, Clarification of Credible Single Contingency, also proposes revisions to the following sections:

- Section 4.3.2

- Section 6.2.2

Proposed Guide Language Revision

2.5.1	Criteria for Removing Contingencies from the Reliability Unit Commitment Analyses

ERCOT shall remove contingencies from the Reliability Unit Commitment (RUC) analysis when:

(a)	The contingency is known to produce post-contingency results that are incorrect; or

(b)	The contingency is known to produce a non-convergent contingency result which may cause the RUC processes to fail.

3.3.3	Resource Entity Responsibilities for Equipment Ratings

(1)	Resource Entities that own Transmission Facilities are responsible for determining the Ratings of its  Transmission Facilities and shall send the methodology used to ERCOT in accordance with the Protocols.  Technical limits established for the operation of Transmission Facilities and associated equipment shall be applied consistently in engineering and planning studies, Real-Time security analyses, and operator actions.

(2)	Resource Entity owners of Transmission Facilities shall provide to ERCOT all nominal Transmission Facility Ratings.

(3)	In operating the ERCOT Transmission Grid, ERCOT shall use these Ratings as follows:

(a)	ERCOT shall limit pre-contingency flows to enforce the Normal Rating.

(b)	If an approved Remedial Action Plan (RAP) is unavailable to unload the Transmission Facility post-contingency, ERCOT shall control the post-contingency loading of the Transmission Facility to levels below the Emergency Rating.  The enforcement shall be implemented in a manner such that the post contingency loading will be at, or below, Normal Rating within two hours.

(c)	If an approved RAP is available, ERCOT shall control the post-contingency loading of the Transmission Facility to levels below the 15-Minute Rating.  The RAP shall be implemented in a manner such that the RAP post-implementation loading will be at, or below, the Emergency Rating within 15 minutes and subsequently, at or below, Normal Rating within two hours.

(d)	ERCOT shall use best efforts to restore all Transmission Facilities to within Normal Ratings as soon as practicable, based on Good Utility Practice.

3.7.2	Transmission Service Provider Responsibilities for Equipment Ratings

(1)	TSPs that own Transmission Facilities are responsible for determining the Ratings of its Transmission Facilities and shall send the methodology used to ERCOT in accordance with  the Protocols.  Technical limits established for the operation of Transmission Facilities and associated equipment shall be applied consistently in engineering and planning studies, Real-Time security analyses, and operator actions.

(2)	TSPs owners of Transmission Facilities shall provide to ERCOT all nominal Transmission Facility Ratings.

(3)	In operating the ERCOT Transmission Grid, ERCOT shall use these Ratings as follows:

(a)	ERCOT shall limit pre-contingency flows to enforce the Normal Rating.

(b)	If an approved Remedial Action Plan (RAP) is unavailable to unload the Transmission Facility post-contingency, ERCOT shall control the post-contingency loading of the Transmission Facility to levels below the Emergency Rating.

(c)	If an approved RAP is available, ERCOT shall control the post-contingency loading of the Transmission Facility to levels below the 15-Minute Rating.  The RAP shall be implemented in a manner such that the RAP post-implementation loading will be at, or below, the  Emergency Rating within 15 minutes and subsequently at, or below, Normal Rating within two hours.

(d)	ERCOT shall use best efforts to restore all Transmission Facilities to within Normal Ratings as soon as practicable, based on Good Utility Practice.

- 4.3.1

- Real-Time and Short Term Planning

ERCOT will conduct Real-Time and short term planning based on the security criteria established in the Protocols and these Operating Guides.  Operations during Forced and Planned Outages will also follow these criteria.  Line Ratings are provided to ERCOT in accordance with Protocols and these Operating Guides.  ERCOT will employ Constraint Management Plans (CMPs) and use of Special Protection Systems (SPSs) to facilitate the use of the ERCOT Transmission Grid while maintaining system security and reliability in accordance with the Protocols, these Operating Guides, and applicable North American Electric Reliability Corporation (NERC) Reliability Standards.  ERCOT will address operating conditions under which the reliability of the ERCOT System is inadequate and no solution is readily apparent in accordance with the Protocols and these Operating Guides.

6.2.2	Design and Operating Requirements for ERCOT System Facilities

(1)	Protective relay systems shall be designed to provide reliability, a combination of dependability and security, so that protective relay systems will perform correctly to remove faulted equipment from the ERCOT System.

(2)	For planned ERCOT System conditions, protective relay systems shall be designed not to trip for swings which do not exceed the steady-state stability limit (note that when out-of-step blocking is used in one location, a method of out-of-step tripping should also be considered).  Protective relay systems shall not interfere with the operation of the ERCOT System under the procedures identified in the other sections of these Operating Guides.

(3)	Any loading limits imposed by the protective relay system shall be documented and followed as an ERCOT System operating constraint.

(4)	The thermal capability of all protection system components shall be adequate to withstand the maximum short time and continuous loading conditions to which the associated protected Transmission elements may be subjected, even as a result of Credible Single Contingency conditions.

(5)	Applicable Institute of Electrical and Electronic Engineers (IEEE)/American National Standards Institute (ANSI) guidelines shall be considered when applying protective relay systems on the ERCOT System.

(6)	The planning and design of generation, transmission and substation configurations shall take into account the protective relay system requirements of dependability, security and simplicity.  If configurations are proposed that require protective relay systems that do not conform to these Operating Guides or to accepted IEEE/ANSI practice, then the Facility owners affected shall negotiate a solution.

(7)	The design, coordination, and maintainability of all existing protective relay systems shall be reviewed periodically by the Facility owner to ensure that protective relay systems continue to meet ERCOT System requirements.  This review shall include the need for redundancy.  Documentation of the review shall be maintained and supplied by the Facility owner to ERCOT or NERC on their request within 30 days.  This documentation shall be reviewed by ERCOT for verification of implementation.

(8)	Upon ERCOT’s request, within 30 days, Generation Entities shall provide ERCOT with the operating characteristics of any generating equipment protective relay systems or controls that may respond to temporary excursions in voltage, frequency, or loading with actions that could lead to tripping of the generator.

(9)	Upon ERCOT’s request, within 30 days, Generation Entities shall provide ERCOT with information that describes how generator controls coordinate with the generator’s short-term capabilities and protective relay systems.

(10)	Over-excitation limiters, when used, shall be coordinated with the thermal capability of the generator field winding.  After allowing temporary field current overload, the limiter shall operate through the automatic AC voltage regulator to reduce field current to the continuous rating.  Return to normal AC voltage regulation after current reduction shall be automatic.  The over-excitation limiter shall be coordinated with the over-excitation protection so that over-excitation protection only operates for failure of the voltage regulator/limiter.  Upon ERCOT’s request, within 30 days, Generation Entities shall provide documentation of coordination.

ERCOT Nodal Operating Guides

Section 11:  Constraint Management Plans and

Special Protection Systems

[DATE]

# 11	CONSTRAINT MANAGEMENT PLANS AND SPECIAL PROTECTION SYSTEMS

11.1	Introduction

(1)	Constraint Management Plans (CMPs) are a set of pre-defined actions executed in response to system conditions to prevent or resolve one or more thermal or non-thermal transmission security violations or to optimize transmission.     CMPs are developed in accordance to the guidelines set forth in the sections below, and are defined in Section 2.1 of the Protocols.  CMPs include, but are not limited to the following:

(a)	Remedial Action Plans (RAPs) which may or may not be modeled in Network Security Analysis (NSA);

(b)	Pre-Contingency Action Plans (PCAPs);

(c)	Temporary Outage Action Plans (TOAPs); and

(d)	Mitigation Plans.

(2)	When developing CMPs, ERCOT shall first attempt to utilize the 15-Minute Rating of the impacted Transmission Facilities, where available, to develop RAPs such that the ERCOT Transmission Grid is utilized to the fullest extent.

(3)	Special Protection Systems (SPSs) may also be implemented in order to allow Generation Resources or Transmission Facilities that would otherwise be subject to restrictions to operate to their full Rating.

(4)	ERCOT shall provide notification to the market of any approved, amended, or removed CMP or SPS.  ERCOT shall post to the Market Information System (MIS) Secure Area all CMPs and SPSs.

(5)	ERCOT shall provide notification to the market of any proposed SPSs or PCAPs on the MIS Secure Area.

(6)	ERCOT is not required to provide notification to the market of any proposed TOAPs.

11.2	Special Protection System

(1)	Special Protection Systems (SPSs) are protective relay systems designed to detect abnormal ERCOT System conditions and take pre-planned corrective actions to maintain a secure system.

(2)	In addition to the requirements in the Protocols and applicable North American Electric Reliability Corporation (NERC) Reliability Standards, SPSs shall also meet the following requirements:

(i)	The SPS owner shall coordinate the design and implementation of the SPS with the owners and operators of Facilities included in the SPS, including but not limited to Generation Resources, TSPs and Direct Current Ties (DC Ties);

(ii)	The SPS shall be automatically armed when appropriate;

(iii)	The SPS shall not operate unnecessarily.  To avoid unnecessary SPS operation, the SPS owner may provide a Real-Time status indication to the owner of any Generation Resource controlled by the SPS to show when the flow on one or more of the SPS monitored Facilities exceeds 90% of the flow necessary to arm the SPS.  The cost necessary to provide such status indication shall be the responsibility of the SPS owner;

(iv)	The status indication of any automatic or manual arming/activation or operation of the SPS shall be provided as Supervisory Control and Data Acquisition (SCADA) alarm inputs to the owners of any Facility controlled by the SPS;

(v)	When an SPS is removed from service, the SPS owner or its Designated Agent shall immediately notify ERCOT.

(vi)	When an SPS is returned to service, the SPS owner or its Designated Agent shall immediately notify ERCOT.  ERCOT shall modify its reliability constraints to recognize the availability of the SPS.

(vii)	The SPS owner shall telemeter the status indication of the following items by SCADA to ERCOT for incorporation into ERCOT systems:

(A)	Any automatic or manual arming/activation or operation of the SPS;

(B)	The in-service/out-of-service status of the SPS; and

(C)	Any additional related telemetry that already exists pertinent to the monitoring of the SPS (e.g. status indication of communications links between associated SPS equipment and the owner’s control center, arming limits of associated SPS equipment).

(viii)	The TSP may receive telemetry for a Resource Entity owned SPS through ERCOT or through the SPS owner, at the option of the TSP.  The SPS owner, at its own cost, must provide telemetry for Resource Entity owned SPSs to the TSP upon request.

(4)	The owners of an existing, modified, or proposed SPS shall submit documentation of the SPS to ERCOT for review and compilation into an ERCOT SPS database.  The documentation shall detail the design, operation, functional testing, and coordination of the SPS with other protection and control systems.

(a)	ERCOT shall conduct a review of each proposed SPS and each proposed modification to an existing SPS.  Additionally, it shall conduct a review of each existing SPS at least every five years as required by changes in system conditions.  Each review shall proceed according to a process and timetable documented in ERCOT Procedures and shall be posted on the MIS Secure Area.

(b)	The review of a proposed SPS shall be completed before the SPS is placed in service, unless ERCOT specifically determines that exemption of the proposed SPS from the review completion requirement is warranted.  The timing of placing the SPS into service must be coordinated with and approved by ERCOT.  The implementation schedule must be confirmed through submission of a Network Operations Model Change Request (NOMCR) to ERCOT.

(c)	Existing SPSs that have already undergone at least one review shall remain in service during any subsequent review.  Modifications to existing SPSs may be implemented upon approval by ERCOT.

(d)	The process and schedule for placing an SPS into service must be consistent with documented ERCOT Procedures.  The schedule must be coordinated among ERCOT and the owners of Facility controlled by the SPS, and shall provide sufficient time to perform any necessary testing prior to its being placed in service.

(e)	ERCOT review of an SPS shall:

(i)	Identify any conflicts with the Protocols, NERC Reliability Standards, and these Operating Guides;

(ii)	Evaluate and document the consequences of failure of a single component of the SPS, which would result in failure of the SPS to operate when required; and

(iii)	Evaluate and document the consequences of misoperation, incorrect operation, or unintended operation of an SPS, when considered by itself and without any other system contingency.

(iv)	Upon completion of ERCOT’s SPS review, ERCOT shall provide all results and underlying studies to the SPS owner.

(f)	If deficiencies are identified by ERCOT or other parties’ comments, the SPS owner shall either submit an amended SPS proposal or withdraw the SPS proposal.  The amended SPS proposal shall undergo the review process specified in (e) above until the identified deficiencies have been resolved to the satisfaction of ERCOT.

(g)	As part of the ERCOT review, ERCOT shall notify the Steady State Working Group (SSWG), the Dynamics Working Group (DWG), and the System Protection Working Group (SPWG) of the SPS proposal, and each working group or any member of each working group may provide any comments, questions, or issues to ERCOT.  ERCOT may work with the owner(s) of Facilities controlled by the SPS as necessary to address all issues.

(h)	ERCOT shall develop a method to include the SPS in Security-Constrained Economic Dispatch (SCED), Outage coordination, and Reliability Unit Commitment (RUC).

(i)	ERCOT’s review shall provide an opportunity for and include consideration of comments submitted by Market Participants affected by the SPS.

11.2.1	Reporting of SPS Operations

(1)	SPS owners shall notify ERCOT of all SPS operations.  Documentation of SPS failures or misoperations shall be provided to ERCOT using the Relay Misoperation Report in Section 8, Attachment B, Relay Misoperation Report.  The SPS owner shall conduct an analysis of all SPS operations, misoperations, and failures.  If deficiencies are identified, a plan to correct the deficiencies shall be developed by the SPS owner subject to the approval of ERCOT, and implemented by the SPS owner.

(2)	ERCOT shall report all SPS operations and misoperations to the Texas Reliability Entity (Texas RE) for review.  SPS arming or activation that ramps generation back is not considered an operation or misoperation with respect to reporting requirements to the Texas RE.  An operation and misoperation of an SPS with respect to reporting requirements to the Texas RE occurs when changes to the transmission system occur, including, but not limited to circuit breaker operation.  Owners of SPSs will provide a monthly report to ERCOT by the 15th of each month describing each instance an SPS armed/activated and reset during the previous month.  The report will include the date and time of arming/activation and reset.  ERCOT shall consolidate the monthly reports and forward to the Texas RE.

(3)	If an SPS which removes generation from service operates more than two times within a six month period and the operations are not a direct result of an ERCOT System disturbance or a contingency operation, ERCOT may require the Generation Resource owner(s) to decrease the available capability on the affected Generation Resource(s).  The amount of available capacity to be decreased shall be determined by ERCOT.  The decreased available capacity on the Generation Resource(s) shall remain until the Generation Resource owner(s) provides documentation that demonstrates the Generation Resource(s) can properly control output in a pre-contingency or normal ERCOT System condition.

(4)	For each SPS, the owner shall either identify a preferred exit strategy or explain why no exit strategy is needed to ERCOT.  This shall take place according to a timetable documented in ERCOT Procedures and posted on the MIS Secure Area.  Once an exit strategy is complete and a SPS is no longer needed, the owner of an existing SPS shall notify ERCOT, whenever the SPS is to be permanently disabled, and shall do so according to a timetable coordinated with and approved by ERCOT and the owners of all Facilities controlled by the SPS.

11.3	Remedial Action Plan

(1)	Remedial Action Plans (RAPs) are defined in Section 2.1, Definitions, of the Protocols and may be relied upon in allowing additional use of the transmission system in SCED.  Normally, it is desirable that a Transmission Service Provider (TSP) constructs Transmission Facilities adequate to eliminate the need for any RAP; however, in some circumstances, such construction may be unachievable in the available time frame.

(2)	RAPs must:

(a)	Be coordinated by ERCOT with all Transmission Operators (TOs) and Resource Entities included in the RAP, and approved by ERCOT;

(b)	Be limited to the time required to construct replacement Transmission Facilities; however, the RAP will remain in effect if ERCOT has determined the replacement Transmission Facilities to be impractical;

(c)	Comply with all applicable requirements in the Protocols and applicable North American Electric Reliability Corporation (NERC) Reliability Standards;

(d)	Clearly define and document TOs and Resource Entities included in the RAP actions;

(e)	Must be able to resolve the issue for which it was designed over the range of conditions that might reasonably be experienced;

(f)	Be executed by the TOs and/or Resource Entities;

(g)	Have a 15-minute Rating greater than the Normal and Emergency Ratings for the Transmission Facilities it intends to resolve;

(h)	Be defined in the Network Operations Model and considered in the Security-Constrained Economic Dispatch (SCED) and Reliability Unit Commitment (RUC).  RAPs that cannot be modeled using ERCOT’s existing infrastructure shall be rejected unless the Technical Advisory Committee (TAC) approves a plan to work around the infrastructure problem; and

(i)	Not include Load shed.

(3)	An approved RAP may be executed immediately after a contingency by the TOs and Resource Entities included in the RAP without instruction by ERCOT or shall be executed upon direction by ERCOT.

(4)	ERCOT shall conduct a review of each existing RAP annually or as required by changes in system conditions to ensure its continued effectiveness.  Each review shall proceed according to a process and timetable documented in ERCOT Procedures.

(5)	ERCOT may approve the expiration of a RAP after consultation with the TOs and Resource Entities included in the RAP.  ERCOT shall modify its reliability constraints to recognize the unavailability of the RAP.

11.3.1	Remedial Action Plan Process

RAPs may be proposed by any Market Participant or may be developed by ERCOT.  For RAPs submitted by Market Participants not registered as a TSP:

(1)	ERCOT shall post RAPs submitted by a Market Participant not registered as a TSP on the MIS Secure Area as soon as practicable, but no later than five Business Days of receipt.

(2)	ERCOT shall provide a five-Business-Day comment period from the date when the proposed RAP under review is posted by ERCOT unless notice of a shorter comment period is provided.

(3)	ERCOT shall consider all comments received within the five-Business-Day comment period on the proposed RAP, along with its own evaluation and those of the Transmission Facility owners, and either approve, modify or reject that proposed RAP.

(4)	If a proposed RAP is modified or rejected, ERCOT shall post an explanation for the rejection or a description of the modification.

11.4	Mitigation Plan

- Mitigation Plans are defined in Section 2.1, Definitions, of the Protocols and shall not be used to manage constraints in SCED by either activating them or deactivating them.  Normally, it is desirable that a Transmission Service Provider (TSP) constructs Transmission Facilities adequate to eliminate the need for a Mitigation Plan; however, in some circumstances, such construction may be unachievable in the available time frame.

(2)	A Mitigation Plan may be proposed by any TSP, but must be approved by ERCOT and the impacted Transmission Operator (TO) prior to implementation.  Mitigation Plans must:

(a)	Be coordinated with the TOs included in the Mitigation Plan;

(b)	Limited in use to the time required to construct replacement Transmission Facilities;  however, the Mitigation Plan will remain in effect if ERCOT has determined the replacement Transmission Facilities to be impractical;

(c)	Comply with all requirements of the Protocols and applicable North American Electric Reliability Corporation (NERC) Reliability Standards;

(d)	Clearly define and document TO actions;

(e)	Be executed by TOs;

(f)	Be able to be implemented in a timeframe that will not result in loss of the overloaded Transmission Facility;

(g)  	Identify the most limiting protective relay setting beyond the 15-Minute Rating when developing the Mitigation Plan in advance or as soon as practicable when developing the Mitigation Plan in Real-Time; and

(h)  	Not subject ERCOT to unacceptable risk of widespread cascading Outages.

(3)	An approved Mitigation Plan may be executed immediately, post-contingency, by the TO without instruction by ERCOT or shall be executed upon direction by ERCOT.

(4)	Restoration of any Load shed by executing the Mitigation Plan shall be coordinated with ERCOT.

11.5	Pre-Contingency Action Plans

- Pre-Contingency Action Plans (PCAPs) are defined in Section 2.1, Definitions, of the Protocols and are implemented in anticipation of a contingency.  Normally, it is desirable that a Transmission Service Provider (TSP) construct Transmission Facilities adequate to eliminate the need for any PCAP; however, in some circumstances, such construction may be unachievable in the available time frame.

(2)	A PCAP may be proposed by any Market Participant, but must be approved by ERCOT and the impacted Transmission Operator (TO) prior to implementation.  PCAPs must:

(a)	Be coordinated with the TOs included in the PCAP;

(b)	Be limited in use to the time required to construct replacement Transmission Facilities and until such Facilities are placed in-service, or the PCAP is no longer needed; however, the PCAP will remain in effect if ERCOT has determined the replacement Transmission Facilities to be impractical;

(c)	Comply with all requirements of the Protocols and applicable North American Electric Reliability Corporation (NERC) Reliability Standards;

(d)	Clearly define and document TO actions;

(e)	Be executed by TOs; and

(f)	Not include Load shed.

(3)	An approved PCAP may be executed immediately prior to a contingency by the TO without instruction by ERCOT, or shall be executed upon direction by ERCOT.

(4)	All proposed, approved, amended, and removed PCAPs shall be managed in accordance with paragraph (4) of Section 11.1, Introduction.

(4)	ERCOT may limit the quantity of PCAPs that are used.

11.5.1	Pre-Contingency Action Plan Process

PCAPs may be proposed by any Market Participant or may be developed by ERCOT.  For PCAPs submitted by Market Participants not registered as a TSP:

(1)	ERCOT shall post PCAPs submitted by a Market Participant not registered as a TSP on the MIS Secure Area as soon as practicable, but no later than five Business Days of receipt.

(2)	ERCOT shall provide a five-Business-Day comment period from the date when the proposed PCAP under review is posted by ERCOT unless notice of a shorter comment period is provided.

(3)	ERCOT shall consider all comments received within the five-Business-Day comment period on the proposed PCAP, along with its own evaluation and those of the Transmission Facility owners, and either approve, modify or reject that proposed PCAP.

(4)	If a proposed PCAP is modified or rejected, ERCOT shall post an explanation for the rejection or a description of the modification

11.6	Temporary Outage Action Plan

(1)	Temporary Outage Action Plans (TOAPs) are defined in Section 2.1, Definitions, of the Protocols and shall not be used to manage constraints in SCED by either activating them or deactivating them.

(2)	A TOAP may be proposed by any Market Participant.  TOAPs shall be approved by ERCOT prior to implementation.  TOAPs must:

(a)	Be coordinated with the TOs included in the TOAP;

(b)	Limit use to the duration of a specific Transmission Facility or Resource Outage;

(c)	Comply with all requirements of  the Protocols and applicable North American Electric Reliability Corporation (NERC) Reliability Standards;

(d)	Clearly define and document TO actions;

(e)	Be executed by TOs;

(f)	Be implemented in a timeframe that will not result in loss of the overloaded Transmission Facility;

(g)  	Identify the most limiting protective relay setting beyond the 15-Minute Rating when developing the TOAP in advance or as soon as practicable when developing the TOAP in Real-Time; and

(h)  	Not subject ERCOT to unacceptable risk of widespread cascading Outages.

(3)	An approved TOAP may be executed immediately, post-contingency, by the TO without instruction by ERCOT or shall be executed upon direction by ERCOT.

(4)	ERCOT may limit the quantity of TOAPs that are used.

(5)	Restoration of any Load shed by executing the TOAP shall be coordinated with ERCOT.