## Slide 1: Comparison of the Operating Reserve Demand Curve & Physical Responsive Capability during the January 6th event
John Dumas
Director of Wholesale Market Operations
TAC
January 28, 2014

## Slide 2: PRC and ORDC were different due to two main factors
@7:10 PRC = 1453 MW and ORDC = 2351MW
The following two factors created the difference
  PRC is limited to 20% of HSL while ORDC considers all the available capacity
    One large unit near LSL due to startup mode which resulted in a 454 MW difference
    Congestion management created a difference
      During the 7:10 SCED interval there were 10 active constraints
      7 of the 10 were violated and were at the max-Shadow Price
      SCED had an under-gen value of 689 MWs (i.e. violating power balance by 689 MWs)
  Load Resources did not update their schedules timely
    Resulted in 140 MW difference

## Slide 3: Managing Constraints with Offers at SWCAP
  At 7:10
    2577 MWs had offers at the SWCAP due to Proxy extensions, Responsive & Regulation offer floors & competitive offers
    41 Resources dispatched down due to congestion management because they had a positive SF to constraints and because they offered part of their capacity at SWCAP
    33 of the 41 Resources contributed 365.2MW to the difference between PRC & ORDC.
    20 of the 33 units contributed about 360MW of the 365.2 MW
    8 of these 20 Resources had offers at SWCAP due to RRS capacity

## Slide 4: Summary
Consider submitting a protocol revision to not count units in startup or shutdown mode in either PRC or ORDC calculations
We have added an additional check to the Load Resource Deployments which will fix the 140 MW error in ORDC going forward. This check was already in place in PRC
Recognize that SCED will dispatch based on economics. SCED will violate power balance if it is cheaper.
  Due to high unit offers in conjunction with congestion contribution (i.e. SCED compares cost of generation plus cost of the transmission penalty to the power balance penalty cost)

## Slide 5: Summary
Part of the Responsive Reserve capacity that was on generation was released automatically to SCED when the frequency dropped below the 59.91Hz trigger.
Responsive Reserve on generation was never manually deployed therefore part of the capacity was never made available to SCED.
  If MWs are trapped behind the HASL SCED can not help with power balance and if more than 20% of a unit’s capability is trapped, it will create a difference between PRC & ORDC
  This can place a greater strain on regulation providers and frequency.