## Slide 1: Response to TAC Questions on PGRR031
TAC– January 28, 2014
Jeff Billo, ERCOT

## Slide 2: PGRR031 Questions from December 3 TAC Meeting
How did OPSTF determine 95% to be the appropriate number to use for PGRR031?
What is the cost of PGRR031?

## Slide 3: Why 95%? (see Appendix 1 for details)
In 2012 ERCOT conducted an analysis to determine the impact of a 90% or 95% criterion on the 2012 Five-Year Transmission Plan 2015 case
Issue | % Loading Variance
Construction Delays | ~2%-5%
Typical wide-area generation unavailability | ~4%
Dynamic ratings on hot days | ~3%
Long-term load forecast error | ?
Transmission outages | Large variation
Total | ?
Criterion | # Elements
Loaded between 90% and 100% | 155
Loaded between 95% and 100% | 40
Numbers reference | #
Total Projects in 2013 Regional Transmission Plan | 105
Total Future Projects in November 2013 TPIT | 621
Total Elements in 2012 Five-Year Transmission Plan 2015 case | ~7000

## Slide 4: PGRR031 Cost Calculation Process
ERCOT conducted an analysis of the final 2016 reliability case from the 2013 Regional Transmission Plan
Disclaimer: ERCOT made assumptions about projects and used generic cost estimates to determine project costs. In order to perform the analysis in a timely manner TSPs were not consulted to verify the accuracy of the assumptions or costs

## Slide 5: PGRR031 impact on 2016 model
61 elements were loaded over 95%
31 of those elements were assumed to drive project accelerations under the PGRR031 criteria
The cost of accelerating these projects was estimated to be $96.35 million
  $54.85 million of that (more than half) was due to the theoretical acceleration of the Houston Import Project from 2018 to 2016.
Details can be found in Appendix 2

## Slide 6: Reliability – Congestion Cost Relationship
Production cost impact of congestion
Price of congestion
Reliability Limit
Constraint Loading
$
*Note: Curves are hypothetical and cost/price curves of a given constraint may differ
Reliability
Economic
Shadow price limit

## Slide 7: Positive cost impacts of PGRR031
 | Total January – November 2013 | At Shadow Price Limit
SCED-binding element intervals | 95,935 | 3,884 (4%)
Congestion rent | $464.8 million | $168.5 million (36%)
 | Total 2012 | At Shadow Price Limit
SCED-binding element intervals | 121,869 | 8,292 (7%)
Congestion rent | $665.9 million | $326.8 million (49%)

## Slide 8: Questions?

## Slide 9: Appendix 1: Background for 95% threshold

## Slide 10: OPSTF issues addressed by PGRR031
#3: Ensuring projects in the Five Year Transmission Plan are completed in a timely manner. This includes unforeseen consideration of load variability, transmission outages and construction complexities that may require earlier completion.
#4a: Appropriate Ratings - Ensure Load and Ratings assumption consistency.
#4c: Appropriate Ratings - Should planning studies be more conservative by using the planning normal rating (Rate A) for a select set of contingencies?
#8c: Generator unit unavailability and modeling issues - Use of “typical” or “historical” Planned, Maintenance and Forced Outages and/or derates in an area

## Slide 11: OPSTF Observations
As OPSTF investigated the issues they identified seven factors that could lead to line overloads in real-time that were not observed in planning studies
The investigation of these factors led to the conclusion that 95% was an appropriate criteria threshold
The following slides detail the OPSTF discussions surrounding these observations

## Slide 12: OPSTF Observation #1
Construction delays for projects planned to resolve a constraint could lead to overloads in Real-Time until the planned project is complete. This could occur for multiple summer seasons depending on the length of the delay.
It was observed that several actual reliability problems experienced in real-time could have been mitigated had planned projects been implemented on time (examples: Moore-Downie in 2012, North-South in 2008 (Clear Springs-Hutto-Salado))
An analysis was conducted using the 2012 Five-Year Transmission Plan. Loading of constraints that exceeded reliability limits in multiple years of the study were found to increase approximately 2% to 3%per year on average with a median of approximately 5%
One alternative approach (to the 95% criterion) was to just plan to implement all projects one year earlier than the identified need. This was eventually dismissed due to compliance implications and the thought that many projects may unnecessarily be accelerated

## Slide 13: OPSTF Observation #2
The current practice to test the unavailability of any given unit in planning studies may miss overloads that occur in operations when multiple units in an area are out of service or derated. Historically over summer peak as much as 10% of capacity in ERCOT has been either derated or unavailable altogether. OPSTF analysis shows that this could increase loadings on circuits by 4% or higher.
OPSTF looked at historic generator outage and derate data for summer peak periods including a presentation given by ERCOT to ROS in September 2011 and data collected by the IMM (see following slide).
OPSTF conducted a study to determine the impact of 10% generation outages over a wide area and found 38 constraints that were loaded higher than just using the current single-unit outage criterion. These constraints generally were loaded 4% higher than without
An approach to develop a wide area generation outage criterion was explored but OPSTF did not come to a consensus on how to implement this consistently across the entire ERCOT system

## Slide 14: Potomac Economics 2003 – 2010 Annual Report related to generator Short-Term Outages and Deratings

## Slide 15: Results of OPSTF analysis

## Slide 16: OPSTF Observation #3
During severe weather that results in higher than anticipated temperatures and higher associated load conditions, facility thermal ratings are generally lowered for studies run by transmission operators per their ambient temperature adjusted dynamic ratings. As an example, one large TSP noted that if the temperature were just 4 degrees F higher than the assumed static rating temperature (104 degrees F) the dynamically rated lines on their system would be rated 3% below the static rating. Since planning reliability studies use static ratings, overloads may be observed in operations under these conditions.
OPSTF explored the possibility of rerating equipment based on a higher (worst-case) assumed temperature. This had implications beyond just circuit ratings and was abandoned

## Slide 17: OPSTF Observation #4
Planning analysis utilizes load forecasts made several years before the operating conditions are realized. Sometimes load grows faster than anticipated and overloads occur in operations because the load level was not seen soon enough in the planning analysis to get the necessary improvements constructed. For example, the recently completed 2012 Five-Year Transmission Plan identified 20 reliability problems for summer 2013 for which the transmission solution for those problems will not be constructed before the problems will occur.
Examples of this include the Valley and oil and gas load
OPSTF did not come up with a feasible alternative to the 95% criterion. There was some discussion of using 90th percentile weather assumptions for load forecast, but this only takes into account load increases due to weather and not economically driven load growth

## Slide 18: OPSTF Observation #5
Planning analysis assumes that all facilities are in-service. However, even over summer peak there is equipment that is out of service for maintenance, construction, or for an extended forced outage. This leads to line loadings in operations that are higher than anticipated in planning studies.
OPSTF did not quantify this effect
Recent planning study process changes at ERCOT are designed to find and solve high consequence n-1-1 contingency constraints, but that does not eliminate low or medium consequence situations
It was observed that other regions in North America plan their systems to be n-1-1 secure (no load loss), but OPSTF did not considered this for ERCOT
The 95% criterion was the only solution that was considered to address this issue

## Slide 19: OPSTF Observations #6 and #7
Actual generation dispatch is different from that modeled in planning cases.
Construction and maintenance clearances are not known when planning studies are performed. During real-time operations, multiple clearances are in effect which cause SCED and RTCA results that differ from planning studies.
These were general observations for which OPSTF did not quantify the effects

## Slide 20: Appendix 2: Details for cost analysis

## Slide 21: Analysis of 2016 case from 2013 RTP
61 non-GSU elements were post-contingency loaded greater than 95%. These were compared against their loading in the final 2018 case from the 2013 RTP
  23 elements either had decreasing or flat loading so I assumed that we would not plan a project for those
  1 element was protected by a non-modeled SPS so I assumed that we would not plan a project for it
  1 element could be fixed by adjusting a phase-shifting transformer so I assumed that we would not plan a project for it
  5 elements had TPIT projects that would be in place by 2015 so I assumed that there would be no acceleration needed
  12 elements had projects (including Houston Import) planned for either 2017 or 2018 so I assumed that they would need to be accelerated to 2016
  The remaining 19 elements did not have projects planned. For these I estimated linear annual loading increases on the elements to determine when they would overload and assumed that the project to solve them would need to be accelerated to 2016. For these projects I estimated the upgrade cost using generic figures

## Slide 22
Results
Disclaimer:
Inclusion or exclusion from this list should not be implied as an ERCOT determination of actual project need. This analysis was conducted solely for the purpose of evaluating the impact of PGRR031. Actual planning analysis may produce different results.

## Slide 23: Cost assumptions
Upgrade cost assumptions:
  69 kV or 138 kV line rebuild = $1M/mile
  345 kV reconductor = $0.5M/ mile
  345/138 kV transformer = $8M
  Terminal equipment upgrade = $1M
Cost of project acceleration assumptions:
  8% discount factor
  3% inflation