DRAFT GMD NOGRR Language

4.7       Geomagnetic Disturbance (GMD) Operating Plan

4.7.1	Monitoring and Dissemination of Space Weather

(1)	ERCOT shall maintain procedures to receive GMD alerts and warnings issued by the National Oceanic and Atmospheric Administration (NOAA)

(2)	ERCOT shall maintain procedures to provide GMD alerts and warnings to Transmission Service Providers (TSPs)

4.7.2	Development and Submission of TSP GMD Operating Plans

(1)	Each TSP that operates Transmission equipment with a voltage of 200kV or higher shall develop a GMD Operating Plan

(2)	This plan shall be provided to ERCOT by {date x} of each year

(3)	The GMD Operating Plan shall include:

a. A procedure to receive GMD alerts and warnings from ERCOT

b. A description of operational actions the TSP intends to take to mitigate the effects of a GMD event.  This description shall include:

1. The triggering event for each action

2. A detailed explanation of each operational action

3. A listing of any actions other entities in the ERCOT Region, including ERCOT, must take in order to implement or coordinate with, the TSP’s GMD Operating Plan

4. The conditions under which each action would be terminated

c. A procedure for reporting to ERCOT any unusual operational information that could be the result of GMD, such as high reactive loading, MVAR or voltage swings of high ground induced current on monitored transformers

4.7.3	ERCOT Review of GMD Operating Plans

(1)	ERCOT shall post its GMD Operating Plan

(2)	The ERCOT GMD Operating Plan shall coordinate the TSP GMD Operating Plans.  This coordination is intended to ensure the TSP GMD Operating Plans are not in conflict with one another; it is not intended to be a technical review of the technical aspects of the TSP GMD Operating Plans.

(3)	The ERCOT GMD Operating Plan should include any operating actions required of ERCOT by the TSP GMD Operating Plans and approved by ERCOT for inclusion in its GMD Operating Plan

(4)	In preparing its GMD Operating Plan, ERCOT should identify any conflicts between the different TSP’s GMD Operating Plans and any unacceptable operating actions required of ERCOT in a TSP’s GMD Operating Plan

a.  Any required modifications to TSPs’ GMD Operating Plans necessary to resolve these conflicts or unacceptable actions should be provided by ERCOT to the appropriate TSPs

b. A TSP shall make the modifications to its GMD Operating Plan required by ERCOT