## Slide 1
Houston Import Project – ERCOT Independent Review
Technical Advisory Committee (TAC)
February 27, 2014
Jeff Billo, ERCOT Transmission Planning

## Slide 2: Background
In July and August 2013 CenterPoint Energy, City of Garland and Cross Texas Transmission, and Lone Star Transmission separately identified a reliability need to increase the import capability into the Houston area by 2018
  Each Transmission Service Provider submitted a project proposal to the Regional Planning Group (RPG) for review and comment
ERCOT conducted a single, combined Independent Review of the proposals

## Slide 3: ERCOT Study Assumptions
ERCOT Independent Review study assumptions are consistent with the 2013 and previous Regional Transmission Plans
  Used the 2018 SE summer peak case
  Generation assumptions per Planning Guide Section 6.9
  Load in Coast, East, Southern, and South Central Weather Zones at peak, all other weather zones scaled down to balance load/ generation
    ERCOT validated this assumption

## Slide 4: Need assessment

## Slide 5: Study Results
Several planning criteria violations found
Singleton-Zenith 345 kV lines are overloaded under N-1
Multiple 345 kV lines (total length ~200 miles) and low voltages under G-1+N-1 conditions

## Slide 6: Load Variations
    Since planning cases model non-coincident peaks for all areas throughout the system and it is not reasonable to expect that all areas will hit their coincident peaks at the same time, it is a reasonable variation of load to scale load down in areas outside of the study area
During RPG discussions stakeholders commented that ERCOT’s load scaling methodology may exacerbate the North-Houston line loading in the 2018 SE study case

## Slide 7: Load Variations cont.
To address stakeholder comments ERCOT analyzed three additional load variations to test the reliability need for a project using the ERCOT Steady-State Working Group (SSWG) cases
  Case 1: 2018 SSWG case (2018 SUM1 Final 10/15/2013) with no changes to load or generation
  Case 2: 2018 SSWG case with outside weather zone load scaled to the highest percentage load level between 2011 and 2013 when the Coast weather zone was at its peak
  Case 3: 2018 SSWG case with outside weather zone load scaled to the percentage of load level when the Coast weather zone was at its peak in 2013

## Slide 8: Load Variation Results
  The result of the G-1+N-1 analysis showed either overload or heavy flow on the existing 345 kV lines from the north into Houston
  The results confirm that the reliability need exists under several different reasonable variations of load
Overload Element (under G-1+N-1) | Case 1 | Case 2 | Case 3*
Singleton-Zenith double circuit | 122% | 128% | 137%
Roans Prairie-Bobville #75 | 99% | 104% | 110%
Bobville-Kuykendahl #75 | 99% | 103% | 110%
Jewett North-Singleton #1 | 93% | 99% | 106%
Jewett South-Singleton #1 | 91% | 97% | 103%
Gibbons Creek-Singleton #75 | 92% | 94% | 101%
Gibbons Creek-Singleton #99 | 92% | 94% | 101%
Jack Creek-Twin Oak #1 | 92% | 100% | 102%
Singleton-Tomball #74 | Below 90% | 93% | 99%
Gibbons Creek-Twin Oak #1 | Below 90% | 92% | 95%
Gibbons Creek-Jack Creek #2 | Below 90% | Below 90% | Below 90%
* Also showed low voltage issue (below 90%) at Tomball 345 kV bus

## Slide 9: Load/ Generation Sensitivity
ERCOT performed an additional sensitivity to determine how much generation additions/ load reduction would be required to defer the identified reliability issues by one year
  Sensitivity performed by scaling down load in Coast weather zone until the thermal violations resolved (to below 100%)
  Result indicated that ~1800 MW reduction would be needed
  Actual generation additions or load reduction may need to be greater depending on shift factors
  Older generation retirement in the Houston area may offset new generation additions

## Slide 10: Need Assessment Summary
ERCOT found several planning criteria violations along the North to Houston 345 kV import pathway
ERCOT confirmed the need using several reasonable variations to load
ERCOT found that a net of approximately 1800 MW of generation addition/ load reduction would defer the need to 2019
  1800 MW represents ~ 6.8% of the total projected load (2018) in the Coastal weather zone

## Slide 11: Project alternatives

## Slide 12: Project Alternative Evaluation
ERCOT evaluated 21 project alternatives to address the identified reliability need (including project proposals from the TSPs)
8 of the projects would resolve the reliability criteria violations:
  Option 1: Twin Oak-Zenith 345 kV with 25% series compensation
  Option 2: Twin Oak-Zenith 345 kV with 50% series compensation
  Option 3: Limestone-Ragan Creek-Zenith 345 kV
  Option 4: Limestone-Gibbons Creek-Zenith 345 kV
  Option 5: Jewett-Jack Creek-Zenith 345 kV
  Option 6: Jewett-Jack Creek-Zenith 345 kV with 25% series compensation
  Option 7: Jewett-Jack Creek-Zenith 345 kV with 50% series compensation
  Option 8: Navarro-Gibbons Creek-Zenith 345 kV

## Slide 13: Map of 21 Alternatives

## Slide 14: Project Alternative Evaluation
ERCOT performed the following analysis to determine which option would best meet the long-term needs of the system:
  Assessment of potential future system upgrades and time value of money analysis of those upgrades
  Voltage stability margin analysis
  System needs analysis if older generation in the Houston area were to retire
  NERC Category C and D contingency analysis
  Production cost savings analysis
  System loss analysis

## Slide 15: Overall Comparison of Options
Description | Option 1 (TWZ-25comp-TA) | Option 2 (TWZ-50comp-TA) | Option 3 (LRZ-TA) | Option 4 (LGZ-TA) | Option 5 (JJZ-TA) | Option 6 (JJZ-25comp-TATJ) | Option 7 (JJZ-50comp-TATJ) | Option 8 (NGZ-TATJ)
System Performance (2018) (All options addressed the reliability need) | Met criteria | Met criteria | Met criteria | Met criteria | Met criteria | Met criteria | Met criteria | Met criteria
Capital cost in 2018 dollar ($ Million), (Based on $3.78 million per mile for T-cost) | 554.8 | 572.0 | 610.2 | 590.1 | 596.3 | 617.1 | 629.1 | 805.9
NPV of the set of future upgrades under each option in 2018 dollar ($ Million) | 387.0 | 390.6 | 399.5 | 383.1 | 652.9 | 419.5 | 435.2 | 537.5
Overall cost impact: Sum of the cost of each option and NPV of future upgrades in 2018 dollar ($ Million) | 941.8 | 962.6 | 1009.7 | 973.3 | 1249.3 | 1036.6 | 1064.4 | 1343.4
Voltage stability Analysis (Estimated 2028 load level in Coast zone = 27931 MW) | 28105 MW (beyond 2028) | 28095 MW (beyond 2028) | 28105 MW (beyond 2028) | 28025 MW (beyond 2028) | 27905 MW (2028) | 28075 MW (beyond 2028) | 28205 MW (beyond 2028) | 28125 MW (beyond 2028)
Performance with the old units offline (AC power flow under N-1) | 4 overloads | 2 overloads | 0 overload | 0 overload | 6 overloads | 2 overload | 0 overload | 3 overloads
Amount of generation reduction from the old units without causing overload under G-1+N-1 (MW) | 900.6 | 911.1 | 1061.3 | 1020.0 | 400.0 | 773.8 | 662.6 | 652.6
NERC Category C and D | Good | Good | Good | Good | Good | Good | Good | Good
Economic Benefit (Relative annual production cost savings in $ million, referenced to Option 8) | 4.3 | 3.4 | 3.2 | 1.7 | 2.1 | 2.2 | 1.7 | 0.0
System Loss Reduction at Peak (MW) | 44.7 | 38.8 | 47.6 | 31.2 | 38.2 | 44.8 | 35 | 32.7
New right of way | 117 mi | 117 mi | 130 mi | 129.9 mi | 128.9 mi | 128.9 mi | 128.9 mi | 177.9 mi
Sub-Synchronous Resonance (SSR) concern | Yes | Yes | No | No | No | Yes | Yes | No

## Slide 16: ERCOT Recommendation
  ERCOT will seek Board of Director endorsement of the following project (Option # 4) as the best option to address both the near-term and long-term reliability needs and to serve the future load in the Houston area:
    Construction of a new Limestone-Gibbons Creek-Zenith 345 kV double circuit to achieve 2988 MVA of emergency rating for each circuit
    Upgrade of the substations at Limestone, Gibbons Creek and Zenith to accommodate the terminations of new transmission lines
    Upgrade of the existing T.H. Wharton-Addicks 345 kV line to achieve 1450 MVA of emergency rating (~10.7 miles)

## Slide 17: QUESTIONS?

## Slide 18: appendix

## Slide 19: Study Base Case
  Total Load in Coast Weather Zone in the 2018 SE case
    ~ 26,355 MW (CNP load = ~ 22800 MW)
    The load is identical to the SSWG case load in the Coastal weather zone
  Status of future generators in the study case
    Online:
      Deer Park Energy G6, Channel Energy GT3,
      Deepwater Energy,
    Offline:
      New W.A. Parish unit, Pondera King, Cobisa

## Slide 20: Case Load Scaling Validation

## Slide 21: Options Evaluated for N-1
ID | CenterPoint Options | Approximate Length (mi)
C1 | Twin Oak-Zenith 345 kV double circuit | 117.0
C2 | Ragan Creek-Zenith double-circuit 345 kV double circuit | 69.0
C3 | Limestone-Ragan Creek-Zenith 345 kV double circuit | 130.2
ID | Lone Star Options | Approximate Length (mi)
L1 | Navarro-Gibbons Creek-Zenith 345 kV double circuit | 165.0
L2 | Navarro-King 345 kV double circuit | 186.0
L3 | Navarro-King 500 kV double circuit | 186.0
L4 | Navarro-King 345 kV double circuit with 50% Series Compensation | 186.0
ID | Cross Texas & Garland Power and Light Options | Approximate Length (mi)
T1 | Gibbons Creek-Tomball 345 kV double circuit | 50.0
T2 | Gibbons Creek-Zenith 345 kV double circuit | 60.0
T3 | Limestone-Gibbons Creek-Zenith 345 kV double circuit | 122.0
ID | ERCOT and Other Options | Approximate Length (mi)
E1 | Jewett-King 345 kV double circuit | 142.5
E2 | Lufkin-Jordan 345 kV double circuit | 126.0
E3 | Fayette-Zenith 345 kV double circuit | 65.6
E4 | Fayette-O'Brien 345 kV double circuit | 73.9
E5 | Jewett-Jack Creek-O'Brien 345 kV double circuit plus loop Twin Oak-Gibbons Creek into Jack Creek | 154.6
E6 | Jewett-Jack Creek-Zenith 345 kV double circuit plus loop Twin Oak-Gibbons Creek into Jack Creek | 134.1
E7 | Sandow-Salem-Zenith 345 kV double circuit | 113.4
E6-a | Jewett-Jack Creek-Zenith 345 kV double circuit with 50% or 25% Series Compensation plus Loop Twin Oak-Gibbons Creek into Jack Creek | 134.1
C1-a | Twin Oak-Zenith 345 kV double circuit with 50% or 25% Series Compensation | 117.0

## Slide 22: Result – N-1 Analysis
Options that did not pass N-1 criteria:
  C2: Ragan Creek-Zenith 345 kV
    Overload of Twin Oak-Ragan Creek 345 kV, Jack Creek-Twin Oak 345 kV
    Heavy flow* on Jewett-Singleton 345 kV
  T1: Gibbons Creek-Tomball 345 kV
    Overload of Jack Creek-Twin Oaks 345 kV
    Heavy flow* on Jewett-Singleton 345 kV
  T2: Gibbons Creek-Zenith 345 kV
    Overload of Jack Creek-Twin Oaks 345 kV
    Heavy flow* on Jewett-Singleton 345 kV
  E2: Lufkin-Jordan 345 kV
    Overload of ~50 miles of 138 kV lines in the Lufkin area
  E3: Fayette-Zenith 345 kV
    Overload of Singleton-Zenith 345 kV
  E4: Fayette-O’Brien 345 kV
    Overload of Singleton-Zenith 345 kV
  * Heavy flow: contingency loading greater than 95%

## Slide 23: Result – G-1+N-1 Analysis
Options that did not meet the G-1+N-1 Analysis:
    C1: Twin Oak-Zenith 345 kV
      Heavy flow* on Singleton-Zenith 345 kV
    E1: Jewett-King 345 kV
      Overload of Singleton-Zenith 345 kV
    E5: Jewett-Jack Creek-O’Brien 345 kV
      Overload of Singleton-Zenith 345 kV
    E7: Sandow-Salem Zenith 345 kV
      Overload of Singleton-Zenith 345 kV
      Heavy flow* on Jewett-Singleton 345 kV
    L3: Navarro-King 500 kV
      Overload of Singleton-Zenith 345 kV
    L4: Navarro-King 345 kV with 50% series compensation
      Overload of Singleton-Zenith 345 kV
    L2: Navarro-King 345 kV
      Overload of Singleton-Zenith 345 kV
      Heavy flow* on Jewett-Singleton 345 kV
  * Heavy flow: contingency loading greater than 95%

## Slide 24: Selected Option for Further Analysis
Eight options selected for further study
  Option 1: Twin Oak-Zenith 345 kV with 25% series compensation (~117 miles)
  Option 2: Twin Oak-Zenith 345 kV with 50% series compensation (~117 miles)
  Option 3: Limestone-Ragan Creek-Zenith 345 kV (~130.2 miles)
  Option 4: Limestone-Gibbons Creek-Zenith 345 kV (~122 miles)
  Option 5: Jewett-Jack Creek-Zenith 345 kV (~134.1 miles)
  Option 6: Jewett-Jack Creek-Zenith 345 kV with 25% series compensation (~134.1 miles)
  Option 7: Jewett-Jack Creek-Zenith 345 kV with 50% series compensation (~134.1 miles)
  Option 8: Navarro-Gibbons Creek-Zenith 345 kV (~165 miles)
Few upgrades of existing lines are also included as part of the options
  For all options above, upgrade
    T.H. Wharton-Addicks 345 kV line (~10.7 miles)
  For Option 6 and 7, upgrade
    Jack Creek-Twin Oak double-circuit 345 kV line (terminal upgrade)
  For Option 8, upgrade
    Jack Creek-Twin Oak 345 kV #1 (terminal upgrade)
These select options moved to the next stage for further evaluation.

## Slide 25: Result of Transfer Capability Analysis (Thermal Overload)
Performed power transfer analysis and identified future thermal upgrades needed for each option over the next 15 years (2028)
Option |  | by 2025 | by 2026 | by 2027 | by 2028
Option 1 | Twin Oak-Zenith w/ 25% compensation plus TH Wharton-Addicks upgrade |  | Singleton-Zenith 345 kV (53.2 mi) | Big Brown-Jewett 345 kV (32.8 mi) | Zenith-TH Wharton 345 kV (15.1 mi)
Option 2 | Twin Oak-Zenith w/ 50% compensation plus TH Wharton-Addicks upgrade |  | Big Brown-Jewett 345 kV (32.8 mi) |  | Singleton-Zenith 345 kV (53.2 mi), Zenith-TH Wharton 345 kV (15.1 mi)
Option 3 | Limestone-Ragan Creek-Zenith plus TH Wharton-Addicks upgrade |  |  | Singleton-Zenith 345 kV (53.2 mi), Jack Creek-Twin Oak #1 (26.7 mi), Big Brown-Jewett 345 kV (32.8 mi) | Gibbons Creek-Ragan Creek 345 kV (9.6 mi)
Option 4 | Limestone-Gibbons Creek-Zenith plus TH Wharton-Addicks upgrade |  |  | Singleton-Zenith 345 kV (53.2 mi), Big Brown-Jewett 345 kV (32.8 mi) | Jack Creek-Twin Oak #1 (26.7 mi)
Option 5 | Jewett-Jack Creek-Zenith plus TH Wharton-Addicks upgrade | Singleton-Zenith 345 kV (53.2 mi) | Big Brown-Jewett 345 kV (32.8 mi), Twin Oak-Jack Creek 345 kV (26.7 mi) |  | Jewett-Singleton 345 kV (49.9 mi), Zenith-TH Wharton 345 kV (15.1 mi), Gibbons Creek-Singleton 345 kV (9.4 mi), Gibbons Creek-Jack Creek 345 kV (21.3 mi)
Option 6 | Jewett-Jack Creek-Zenith w/ 25% compensation plus TH Wharton-Addicks & Twin Oak-Jack Creek upgrade |  | Big Brown-Jewett 345 kV (32.8 mi) | Singleton-Zenith 345 kV (53.2 mi) | Zenith-TH Wharton 345 kV (15.1 mi), Twin Oak-Jack Creek 345 kV (26.7 mi)
Option 7 | Jewett-Jack Creek-Zenith w/ 50% compensation plus TH Wharton-Addicks & Twin Oak-Jack Creek upgrade |  | Big Brown-Jewett 345 kV (32.8 mi) |  | Singleton-Zenith 345 kV (53.2 mi), Zenith-TH Wharton 345 kV (15.1 mi), Twin Oak-Jack Creek 345 kV (26.7 mi)
Option 8 | Navarro-Gibbons Creek-Zenith plus TH Wharton-Addicks & Twin Oak-Jack Creek upgrade |  | Jewett-Singleton 345 kV (49.9 mi), Gibbons Creek-Twin Oak & Gibbons Creek-Jack Creek-Twin Oak 345 kV (48 mi) | Singleton-Zenith 345 kV (53.2 mi) | 

## Slide 26: Result of Transfer Capability Analysis (Voltage Stability)
MW load level at the point of voltage collapse under each select option without any upgrades
Voltage collapse occurs beyond 2028 under every option except Option 5

## Slide 27: Impact of Old Generator Retirement
11 units (total 1939 MW) are more than 50 year old by 2018
  Sam Bertron G1, G2, G3, G4 and GT2
  T.H. Warton GT1
  W.A. Parish G1, G2, G3, G4, and GT1
Result of AC power flow analysis with all these 50-year old units offline
  System problems in the 2018 base case either under system intact or N-1 conditions:
    Under system intact condition with the units offline,
      Overload of Singleton-Zenith 345 kV line
      Overload of Jewett-Singleton 345 kV line
      Low voltage around Tomball, Kuykendahl, Bobville, Rothwood
    Under N-1 contingency conditions,
      Overload of Jewett-Singleton 345 kV line
      Overload of the bus ties at Twin Oak/Oak Grove
      Overload of Singleton-Zenith 345 kV line
      Overload of Gibbons Creek-Twin Oak 345 kV line
      Overload of Jack Creek-Twin Oak 345 kV line
      Overload of Gibbons Creek-Singleton 345 kV line
      Overload of Roans Prairie-Bobville-Kuykendahl 345 kV line
      Heavy flow on Singleton-Tomball and Gibbons Creek-Jack Creek 345 kV line
      Low voltages at 15 345-KV buses and 38 138-kV buses in Houston area

## Slide 28: Impact of Old Generator Retirement
Result of AC power flow analysis with each option:
  No system problem under system intact condition
  No low voltage issues under N-1 condition
  Table below shows overload and heavy flow issues under N-1 conditions when the old units are offline
Elements | Jewett S-Singleton 345 kV line #1 | Jewett N-Singleton 345 kV line #1 | Twin Oak-Oak Grove 345 kV bus tie | Twin Oak 345 kV bus tie | Singleton-Zenith 345 kV line #98 | Singleton-Zenith 345 kV line #99 | Gibbons Creek-Twin Oak 345 kV #1 | Gibbons Creek-Jack Creek 345 kV #2 | Jack Creek-Twin Oak 345 kV #1 | Jack Creek-Twin Oak 345 kV #2
Option 1 |  |  | Overload | Overload | Overload | Overload |  |  |  | 
Option 2 |  |  | Overload | Overload |  |  |  |  |  | 
Option 3 |  |  | Heavy flow | Heavy flow | Heavy flow | Heavy flow |  |  | Heavy flow | 
Option 4 |  |  | Heavy flow | Heavy flow | Heavy flow | Heavy flow |  |  |  | 
Option 5 |  |  | Overload | Overload | Overload | Overload |  |  | Overload | Overload
Option 6 |  |  | Overload | Overload | Heavy flow | Heavy flow |  |  |  | 
Option 7 |  |  | Heavy flow | Heavy flow |  |  |  |  | Heavy flow | Heavy flow
Option 8 | Overload | Overload | Heavy flow | Heavy flow | Heavy flow | Heavy flow | Overload | Heavy flow | Heavy flow | 

## Slide 29: Impact of Old Generator Retirement
Result of generation reduction analysis:
  Tested G-1+N-1 while reducing the output from the old units
  Estimated total MW output that can be reduced from the old unit under each select option without causing any thermal issues
Option | Description | Approximate MW generation reduction that starts causing overload under G-1+N-1
Option 1 | Twin Oak-Zenith with 25% series compensation plus TH Wharton-Addicks upgrade | 900.6
Option 2 | Twin Oak-Zenith with 50% series compensation plus TH Wharton-Addicks upgrade | 911.1
Option 3 | Limestone-Ragan Creek-Zenith plus TH Wharton-Addicks upgrade | 1061.3
Option 4 | Limestone-Gibbons Creek-Zenith plus TH Wharton-Addicks upgrade | 1020.0
Option 5 | Jewett-Jack Creek-Zenith plus TH Wharton-Addicks upgrade | 400.0
Option 6 | Jewett-Jack Creek-Zenith with 25% series compensation plus TH Wharton-Addicks upgrade and Twin Oak-Jack Creek upgrade | 773.8
Option 7 | Jewett-Jack Creek-Zenith with 50% series compensation plus TH Wharton-Addicks upgrade and Twin Oak-Jack Creek upgrade | 662.6
Option 8 | Navarro-Gibbons Creek-Zenith plus TH Wharton-Addicks upgrade and Twin Oak-Jack Creek upgrade | 652.6

## Slide 30: Impact of NERC Category C and D
Tested 23 severe events (NERC Cat. C and D contingencies) based on the past study and knowledge of the system
Options | Description | # of Unsolved Contingencies (NERC Cat. D) | Thermal Overload 345 kV 115% above | Low Voltage At 345 kV Buses ( below 0.9 pu)
 | Base Case | 6 | 6 | 5
Option 1 | Twin Oak-Zenith with 25% series compensation plus TH Wharton-Addicks upgrade | 1 | 1 | 4
Option 2 | Twin Oak-Zenith with 50% series compensation plus TH Wharton-Addicks upgrade | 1 | 0 | 3
Option 3 | Limestone-Ragan Creek-Zenith plus TH Wharton-Addicks upgrade | 1 | 0 | 5
Option 4 | Limestone-Gibbons Creek-Zenith plus TH Wharton-Addicks upgrade | 1 | 0 | 5
Option 5 | Jewett-Jack Creek-Zenith plus TH Wharton-Addicks upgrade | 1 | 1 | 6
Option 6 | Jewett-Jack Creek-Zenith with 25% series compensation plus TH Wharton-Addicks upgrade and Twin Oak-Jack Creek upgrade | 1 | 0 | 5
Option 7 | Jewett-Jack Creek-Zenith with 50% series compensation plus TH Wharton-Addicks upgrade and Twin Oak-Jack Creek upgrade | 1 | 0 | 3
Option 8 | Navarro-Gibbons Creek-Zenith plus TH Wharton-Addicks upgrade and Twin Oak-Jack Creek upgrade | 1 | 0 | 5

## Slide 31: System Loss Reduction
System losses with each option modeled in the 2018 summer peak study case were compared to the base case
In every option, significant loss reduction is expected
Option | Option 1 (TWZ-25%COMP-TA) | Option 2 (TWZ-50%COMP-TA) | Option 3 (LRZ-TA) | Option 4 (LGZ-TA) | Option 5 (JJZ-TA) | Option 6 (JJZ-25%COMP-TATJ) | Option 7 (JJZ-50%COMP-TATJ) | Option 8 (NGZ-TATJ)
System Loss Reduction (MW) | 44.7 | 38.8 | 47.6 | 31.2 | 38.2 | 44.8 | 35 | 32.7

## Slide 32: Sensitivity Analyses for Transfer Study
  A sensitivity analysis was performed using the latest SSWG case
    Case used: As-built 2014 SSWG Data Set B 2018 base case
    Results confirmed overload on Singleton-Zenith 345 kV double circuit line under the G-1+N-1 condition
  Power transfer analysis using different load scaling approach
    Power transfer analysis was performed for certain options under N-1 conditions using the following two load scaling approaches:
      Scaling load down in North, North Central, West and Far West
      Scaling all load down except the load in Coast Weather Zone
    The result indicates that:
      There are reliability criteria violations in 2018 regardless of which approach is used
      The need identification for the next set of upgrades may be deferred by a year or two if the all-load-scaling (#2) approach is used
        For example, roughly 220~300 MW difference in the transfer capability, when the future overload issue on the Singleton-Zenith double-circuit 345 kV line occurs with each option

## Slide 33: Cost Analysis
  Methodology and Assumptions:
    In addition to the cost of each select option, the cost of each future upgrade (up to 2028) was also considered to capture the long-term reliability benefit of each select option.
    Overall cost associated with each select option was calculated.
    Overall cost = Construction cost* of each select option +
    NPV† of construction cost** of future upgrades
    * the construction cost of each select option in 2018 dollar.
    ** the future value of each future upgrade, estimated by using 3% inflation
    rate.
    † 8% discount rate was used to calculate the NPV (in 2018 dollar) of the set
    of future upgrades under each select option.
    (Reference of discount rate: www.puc.texas.gov/industry/electric/reports/31600/PUCT_CBA_Report_Final.pdf)

## Slide 34: Result of Cost Analysis
Option | Construction Cost * of Each Select Option (in 2018 dollar) | Net Present Value (NPV) of Construction Cost of the Set of Future Upgrades (in 2018 dollar) | Overall Cost (in 2018 dollar)
Option 1 (TWZ-25%) | 554.8 | 387.0 | 941.8
Option 2 (TWZ-50%) | 572.0 | 390.6 | 962.6
Option 3 (LRZ) | 610.2 | 399.5 | 1,009.7
Option 4 (LGZ) | 590.1 | 383.1 | 973.3
Option 5 (JJZ) | 596.3 | 652.9 | 1,249.3
Option 6 (JJZ-25%) | 617.1 | 419.5 | 1,036.6
Option 7 (JJZ-50%) | 629.1 | 435.2 | 1,064.4
Option 8 (NGZ) | 805.9 | 537.5 | 1,343.4
Unit: $ Million
Unit: $ Million
* $ 3.78 million-per-mile was assumed for T-line portion of the cost. ERCOT performed sensitivity analysis
using different cost-per-mile assumption. No significant impact was found in selecting a best solution.

## Slide 35: Result of Cost Analysis
Unit: $ Million

## Slide 36: Economic Analysis
Unit: $ Million
  Although the Houston Import RPG review is purely driven by reliability need, ERCOT also performed an economic analysis for the year 2018 using the 2018 economic case.
  Relative annual production cost of each option was obtained by comparing the annual production cost of each option against the option with the highest annual production cost.
Option | Option 1 | Option 2 | Option 3 | Option 4 | Option 5 | Option 6 | Option 7 | Option 8
Relative Production cost savings (Referenced to Option 8) | 4.3 | 3.4 | 3.2 | 1.7 | 2.1 | 2.2 | 1.7 | 0.0
Unit: $ Million