## TitlePage
Report on the Capacity, Demand, and Reserves in the ERCOT Region February 2014

## Contents
Contents
Tab | Notes
Disclaimer | Please read.
Definitions | List of definitions
Changes from 2013 CDR (May 2013) | List of changes from the 2013 CDR (May 2013)
Executive Summary | Synopsis of considerations for this report
SummerSummary | Shows load forecast, generation resources, and reserve margin for Summer 2014 through Summer 2023
SummerCapacities | Lists units and their capabilities used in determining the generation resources in the Summer Summary
WinterSummary | Shows load forecast, generation resources, and reserve margin for Winter 2014 through Winter 2023
WinterCapacities | Lists units and their capabilities used in determining the generation resources in the Winter Summary
SummerFuelTypes | Lists generation fuel types by MW and by percentage for Summer 2014 through Summer 2023
WinterFuelTypes | Lists generation fuel types by MW and by percentage for Winter 2014 through Winter 2023

## Disclaimer
Disclaimer
CDR WORKING PAPER
FOR PLANNING PURPOSES ONLY
This ERCOT Working Paper has been prepared for specific ERCOT and market participant purposes and has been developed from data provided by ERCOT market participants. The data may contain errors or become obsolete and thereby affect the conclusions and opinions of the Working Paper. ERCOT MAKES NO WARRANTY, EXPRESS OR IMPLIED, INCLUDING ANY WARRANTY OF MERCHANTABILITY OR FITNESS FOR ANY PARTICULAR PURPOSE, AND DISCLAIMS ANY AND ALL LIABILITY WITH RESPECT TO THE ACCURACY OF SAME OR THE FITNESS OR APPROPRIATENESS OF SAME FOR ANY PARTICULAR USE. THIS ERCOT WORKING PAPER IS SUPPLIED WITH ALL FAULTS. The specific suitability for any use of the Working Paper and its accuracy should be confirmed by each ERCOT market participant that contributed data for this Working Paper.
This Working Paper is based on data submitted by ERCOT market participants as part of their Annual Load Data Request (ALDR) and their resource asset registration and on data in the EIA-411. As such, this data is updated on an ongoing basis, which means that this report can be rendered obsolete without notice.

## Definitions
Definitions
Available Mothballed Generation
Mothballed capacity with a return-to-service probability of 50% or greater for the given year, as provided by its owner, constitutes available mothballed generation. Return probabilities are considered protected information under the ERCOT Protocols and therefore are not included in this report.
Effective Load-Carrying Capability (ELCC) of Wind Generation
The value is 8.7% of the nameplate capacity listed in the Summer Capacities and Winter Capacities tables, both for installed capacity and planned capacity.
Forecast Zone
Forecast Zones have the same boundaries as the 2003 ERCOT Congestion Management Zones. Each Resource is mapped to a Forecast Zone during the registration process.
LRs (Load Resources)
Load capable of reducing or increasing the need for electrical energy or providing Ancillary Services to the ERCOT System, as described in the ERCOT Protocols, Section 6, Ancillary Services. These Resources may provide the following Ancillary Services: Responsive Reserve Service, Non-Spinning Reserve Service, Replacement Reserve Service, and Regulation Service. The Resources must be registered and qualified by ERCOT and will be scheduled by a Qualified Scheduling Entity (QSE).
Mothballed Capacity
The difference in the available mothballed generation (see definition above) and the total mothballed capacity.
Mothballed Unit
A generation resource for which a generation entity has submitted a Notification of Suspension of Operations, for which ERCOT has declined to execute an RMR agreement, and for which the generation entity has not announced retirement of the generation resource. A seasonal mothballed unit is one in which the generation entity requests a seasonal operation period that must include June 1 through September 30.
Net Dependable Capability
Maximum sustainable capability of a generation resource as demonstrated by performance testing. Certain resource capacities cited in this report, such as for hydro and DC Tie imports, use the capability measure referred to as the High Sustained Limit (HSL). The HSL is continuously updated in Real-Time and reported to ERCOT in Current Operation Plans by QSEs.
Non-Synchronous Tie
Any non-synchronous transmission interconnection between ERCOT and non-ERCOT electric power systems.
Other Potential Resources
Capacity resources that include one of the following:
• Remaining "mothballed" capacity not included as resources in the reserve margin calculation
• Remaining DC tie capacity not included as resources in the reserve margin calculation, and
• New generating units that have initiated full transmission interconnection studies through the ERCOT generation interconnection process (Note that new wind units would be included based on the appropriate discounted capacity value applied to existing wind generating units.)
Planned Units in Full Interconnection Study Phase
To connect new generation to the ERCOT grid, a generation developer must go through a set procedure. The first step is a high-level screening study to determine the effects of adding the new generation on the transmission system. The second step is the full interconnection study. These are detailed studies done by the transmission owners to determine the effects of the addition of new generation on the transmission system.
Private Networks
An electric network connected to the ERCOT transmission grid that contains load that is not directly metered by ERCOT (i.e., load that is typically netted with internal generation).
Reliability Must-Run (RMR) Unit
A generation resource unit operated under the terms of an agreement with ERCOT that would not otherwise be operated except that they are necessary to provide voltage support, stability or management of localized transmission constraints under first contingency criteria.
Signed IA (Interconnection Agreement)
An agreement that sets forth requirements for physical connection between an eligible transmission service customer and a transmission or distribution service provider.
Switchable Unit
A generation resource that can be connected to either the ERCOT transmission grid or a grid outside the ERCOT Region.

## Changes
Changes from 2013 CDR (May 2013)
1 | Peak Demand based on the February 2014 load forecast.
2 | Energy Efficiency is included in Total Peak Demand; Line 5 is now TDSP Standard Offer Load Management Programs only.
3 | Commercial operation dates for Panda Sherman project and Panda Temple I project (1,437 MW) were revised from early summer 2014 to late summer 2014.
4 | All SR Bertron units (727 MW) moved to Mothballed status from Operational status.
5 | J T Deely Units 1 and 2 (845 MW) moved from Retired status to Mothballed status starting in 2019.
6 | Thomas C Ferguson 1 (354 MW) retired in September 2013.
7 | Deepwater Energy Storage (40 MW; planned; 10INR0089) removed from Planned status to Cancelled status.
8 | AES Deepwater Storage (APD_APD_PS1; 1 MW; Harris County) moved from Operational status to Retired status.
9 | Martin Lake 3 (805 MW) moved from Operational status to Seasonal Mothballed status.
10 | Monticello Units 1 and 2 (1,070 MW) moved from Operational status to Seasonal Mothballed status.
11 | Non-Coastal and Coastal Wind Capacity shown separately with 8.7% Effective Load Carrying Capability (ELCC) for both Non-Coastal and Coastal Wind Capacity.
12 | The following projects moved from Planned status to Operational status.
| Project Name | Unit_Code | County | Fuel | MW Capacity
| SANDY CREEK 1 | SCES_UNIT1 | MCLENNAN | COAL | 970
| PETRO NOVA - WA PARISH | PNPI_GT2 | FORT BEND | GAS | 74
| ACACIA SOLAR | ACACIA_UNIT_1 | PRESIDIO | SOLAR | 9.99
| OCI ALAMO 1 | OCI_ALM1_UNIT1 | BEXAR | SOLAR | 39.183
| BLUE SUMMIT WIND 5 | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND | 9
| BLUE SUMMIT WIND 6 | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND | 126.4
| LOS VIENTOS WIND I | LV1_LV1A | WILLACY | WIND | 200.1
| LOS VIENTOS WIND II | LV1_LV1B | WILLACY | WIND | 201.6
13 | The following projects have finalized the necessary agreements and permits to be added to CDR:
| Project Name | GINR | County | Fuel | Year In Service | MW Capacity
| RENTECH PROJECT | 13INR0040 | HARRIS | GAS | 2014 | 15
| FORNEY POWER UPGRADE | 14INR0059 | KAUFMAN | GAS | 2014/2015 | 52
| WHITE CAMP SOLAR | 11INR0094 | KENT | SOLAR | 2014 | 100
| MUSTANG SOLAR PROJECT | 13INR0031 | TRAVIS | SOLAR | 2015 | 30
| OCI ALAMO 4 | 14INR0024 | KINNEY | SOLAR | 2014 | 37.6
| PECOS BARILLA SOLAR | 12INR0059 | PECOS | SOLAR | 2014 | 30
| BRISCOE WIND FARM | 14INR0072 | BRISCOE | WIND | 2015 | 300
| CAMERON COUNTY WIND | 11INR0057 | CAMERON | WIND | 2014 | 165
| COMANCHE RUN WIND | 12INR0029 | SWISHER | WIND | 2016 | 500
| CPV RATTLESNAKE DEN PH 1 | 13INR0020a | GLASSCOCK | WIND | 2014 | 200
| CPV RATTLESNAKE DEN PH 2 | 13INR0020b | GLASSCOCK | WIND | 2016 | 150
| GREEN PASTURES WIND | 12INR0070 | KNOX | WIND | 2015 | 300
| HEREFORD WIND a | 13INR0059a | CASTRO | WIND | 2015 | 200
| JUMBO ROAD WIND b | 13INR0059b | CASTRO | WIND | 2015 | 300
| KEECHI WIND 138 KV JOPLIN | 14INR0049_2 | JACK | WIND | 2014 | 102
| LOGANS GAP WIND I | 13INR0050 | COMANCHE | WIND | 2015 | 200
| LOS VIENTOS III | 13INR0052 | STARR | WIND | 2014 | 200
| MIAMI WIND 1b | 14INR0012b | GRAY | WIND | 2015 | 111
| PAMPA WIND PROJECT | 12INR0018 | GRAY | WIND | 2017 | 500
| PATRIOT (PETRONILLA) WIND | 11INR0062 | NUECES | WIND | 2016 | 178
| ROUTE66 WIND | 14INR0032a | RANDALL | WIND | 2015 | 150
| SENDERO WIND ENERGY PROJECT | 12INR0068 | JIM HOGG | WIND | 2015 | 78
| SOUTH PLAINS WIND I | 14INR0025a | FLOYD | WIND | 2015 | 200
| SOUTH PLAINS WIND II | 14INR0025b | FLOYD | WIND | 2015 | 300
| SPINNING SPUR WIND THREE | 14INR0053 | OLDHAM | WIND | 2014 | 194
| WINDTHORST 2 | 13INR0057 | ARCHER | WIND | 2014 | 65

## Executive_Summary
Executive Summary
The methodology for developing this report is defined in Chapter 3 of the ERCOT Protocols (see: http://www.ercot.com/content/mktrules/nprotocols/current/03-040213_Nodal.doc). ERCOT has developed this report using data provided by resource owners and by transmission service providers. Although ERCOT works to ensure that the data provided are as accurate and current as possible, we cannot independently verify all of the information provided to us. Information available to ERCOT as of February 21, 2014, is included in this report. The load forecast included in this assessment has been developed with a revised load forecast methodology that uses customer accounts (residential, commercial and industrial) that relate to relevant economic indicators for each of those customer classes within the ERCOT region. This load model forecasts peak loads and total annual customer demand based on an average of the past 12 years of weather conditions. In contrast, the next Seasonal Assessment of Resource Adequacy (SARA) reports, which will be released on March 5, 2014, cover a range of scenarios including extremely high load and generation outages. The new model also accounts for energy efficiency impacts on the historical summer peaks, and therefore a separate energy efficiency line item is no longer included in this report to avoid double-counting the load impacts. Additional information regarding the revised load forecasting methodology is available at: http://www.ercot.com/gridinfo/load/. Currently available information indicates that the planning reserve margin in the ERCOT region will be approximately 13 percent at the start of the 2014 peak season and will rise to 16 percent when the Panda Sherman (720 MW), Panda Temple I (717 MW), Ferguson (510 MW), and Deer Park Energy Center (165 MW) combined-cycle gas plants are completed and brought into service later in the summer season. (The commercial operations date for the Deer Park plant is currently July 1, 2014, while the date for the Panda and Ferguson plants is currently August 1, 2014). The expected wind capacity availability for coastal and non-coastal resource locations is being reported separately due to their differing operational characteristics. For example, the availability of coastal resources is typically significantly higher than non-coastal resources during peak load conditions due to the prevailing coastal wind patterns during late summer afternoons. Note that capacity for all wind generation resources are being included in the report at 8.7 percent of the total nameplate capacity. ERCOT acknowledges that the 8.7 percent peak load capacity availability is conservative. Recent analysis indicates that wind generation resources in ERCOT can be expected to serve peak demand at levels of approximately 27 percent of nameplate capacity for wind generation resources located along the Texas Gulf Coast, and 14 percent of nameplate capacity for other wind generation resources. ERCOT is also considering other methods of estimating the capacity availability of wind, such as using historical operational availability, and will adopt the most desirable method for future CDR reports. The ERCOT protocols were modified in NPRR 550 (approved by the ERCOT Board of Directors on November 19, 2013) to include a requirement that thermal power plants have received their greenhouse-gas air emissions permit to be included in the CDR report. Currently five natural gas-fired powerplants have received an interconnection agreement for transmission service, but have not completed their air permitting requirements. Therefore, those facilities are not included in this report. Those future power plants are: Antelope facility (394 MW, currently scheduled to be completed July 2016); Goldsmith Peaking facility (380 MW, currently scheduled to be completed June 2015); P.H. Robinson Peaking facility (388 MW, currently scheduled to be completed April 2015); Friendswood Energy Generation (316 MW, currently scheduled to be completed September 2015); FGE Texas facility (799 MW, currently scheduled to be completed June 2016).

## SummerSummary
2014 Report on the Capacity, Demand, and Reserves in the ERCOT Region
Summer Summary
Load Forecast: |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023
| Total Summer Peak Demand, MW | 68096 | 69057 | 70014 | 70871 | 71806 | 72859 | 73784 | 74710 | 75631 | 76550
| less LRs Serving as Responsive Reserve, MW | 1230.6203 | 1230.6203 | 1230.6203 | 1230.6203 | 1230.6203 | 1230.6203 | 1230.6203 | 1230.6203 | 1230.6203 | 1230.6203
| less LRs Serving as Non-Spinning Reserve, MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| less Emergency Response Service (10- and 30-min ramp products) | 431.4841 | 432.196 | 432.196 | 432.196 | 432.196 | 432.196 | 432.196 | 432.196 | 432.196 | 432.196
| less TDSP Standard Offer Load Management Programs | 254.8243 | 254.8243 | 254.8243 | 254.8243 | 254.8243 | 254.8243 | 254.8243 | 254.8243 | 254.8243 | 254.8243
| Firm Load Forecast, MW | 66179.0713 | 67139.3593 | 68096.3593 | 68953.3593 | 69888.3593 | 70941.3593 | 71866.3593 | 72792.3593 | 73713.3593 | 74632.3593
Resources: |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023
| Installed Capacity, MW | 63114.529 | 63114.529 | 63114.529 | 63114.529 | 63114.529 | 62274.529 | 62274.529 | 62274.529 | 62274.529 | 62274.529
| Capacity from Private Networks, MW | 4655 | 4655 | 4655 | 4655 | 4655 | 4655 | 4655 | 4655 | 4655 | 4655
| Effective Load-Carrying Capability (ELCC) of Non-Coastal Wind (8.7%), MW | 816.2972 | 816.2972 | 816.2972 | 816.2972 | 816.2972 | 816.2972 | 816.2972 | 816.2972 | 816.2972 | 816.2972
| Effective Load-Carrying Capability (ELCC) of Coastal Wind (8.7%), MW | 146.4253 | 146.4253 | 146.4253 | 146.4253 | 146.4253 | 146.4253 | 146.4253 | 146.4253 | 146.4253 | 146.4253
| RMR Capacity to be under Contract, MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operational Generation, MW | 68732.2516 | 68732.2516 | 68732.2516 | 68732.2516 | 68732.2516 | 67892.2516 | 67892.2516 | 67892.2516 | 67892.2516 | 67892.2516
| Capacity Contribution of Non-Synchronous Ties (top 20 hrs), MW | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3
| Switchable Capacity, MW | 2972 | 2972 | 2972 | 2972 | 2972 | 2972 | 2972 | 2972 | 2972 | 2972
| Available Mothballed Capacity, MW | 2602 | 2660 | 1933 | 1933 | 1933 | 1933 | 1933 | 1933 | 1933 | 1933
| Planned Resources (not wind) with Signed IA and Air Permit, MW | 130 | 2320.6 | 3093.6 | 3093.6 | 4562.2 | 4802.2 | 4802.2 | 4802.2 | 4802.2 | 4802.2
| ELCC of Planned Non-Coastal Wind with Signed IA (8.7%), MW | 26.9352 | 432.7815 | 568.7625 | 670.3785 | 670.3785 | 670.3785 | 670.3785 | 670.3785 | 670.3785 | 670.3785
| ELCC of Planned Coastal Wind with Signed IA (8.7%), MW | 0 | 31.929 | 61.422 | 61.422 | 61.422 | 61.422 | 61.422 | 61.422 | 61.422 | 61.422
| Total Resources, MW | 75106.4868 | 77792.8621 | 78004.3361 | 78105.9521 | 79574.5521 | 78974.5521 | 78974.5521 | 78974.5521 | 78974.5521 | 78974.5521
| less Switchable Capacity Unavailable to ERCOT, MW | -300 | -300 | -300 | -300 | -300 | -300 | -300 | 0 | 0 | 0
less Retiring Capacity, MW | bar: 2014 to 2023
| Resources, MW | 74805.4868 | 77491.8621 | 77703.3361 | 77804.9521 | 79273.5521 | 78673.5521 | 78673.5521 | 78973.5521 | 78973.5521 | 78973.5521
| Reserve Margin | 13.03% | 15.42% | 14.11% | 12.84% | 13.43% | 10.9% | 9.472% | 8.492% | 7.136% | 5.817%
(Resources - Firm Load Forecast)/Firm Load Forecast
2014 Report on the Capacity, Demand, and Reserves in the ERCOT Region
Summer Summary
|  | 75278.6936 | 76371.0212 | 77459.6087 | 78434.4462 | 79498.0087 | 80695.7962 | 81747.9837 | 82801.3087 | 83848.9462 | 84894.3087

## SummerCapacities
Unit Capacities - Summer
Units used in determining the generation resources in the Summer Summary
Operational capacities are based on unit testing. Other capacities are based on information provided by the plant owners. This list includes MW available to the grid from private network (self-serve) units. It also includes distributed generation units that have registered with ERCOT. Data without unit names are for private network units or are planned generation that is not public.
[7 empty] | Summer | Summer | Summer | Summer | Summer | Summer | Summer | Summer | Summer | Summer
SITE_NAME | GINR_NUM | UNIT_CODE | COUNTY | FUEL | ZONE | YEAR | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023
BIG BROWN 1 |  | BBSES_UNIT1 | FREESTONE | COAL | NORTH | 1971 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
BIG BROWN 2 |  | BBSES_UNIT2 | FREESTONE | COAL | NORTH | 1972 | 595 | 595 | 595 | 595 | 595 | 595 | 595 | 595 | 595 | 595
COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650
FAYETTE POWER PROJECT 1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 604 | 604 | 604 | 604 | 604 | 604 | 604 | 604 | 604 | 604
FAYETTE POWER PROJECT 2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 599 | 599 | 599 | 599 | 599 | 599 | 599 | 599 | 599 | 599
FAYETTE POWER PROJECT 3 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 441 | 441 | 441 | 441 | 441 | 441 | 441 | 441 | 441 | 441
GIBBONS CREEK 1 |  | GIBCRK_GIB_CRG1 | GRIMES | COAL | NORTH | 1983 | 470 | 470 | 470 | 470 | 470 | 470 | 470 | 470 | 470 | 470
J K SPRUCE 1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 555 | 555 | 555 | 555 | 555 | 555 | 555 | 555 | 555 | 555
J K SPRUCE 2 |  | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 775 | 775 | 775 | 775 | 775 | 775 | 775 | 775 | 775 | 775
J T DEELY 1 |  | CALAVERS_JTD1 | BEXAR | COAL | SOUTH | 1977 | 420 | 420 | 420 | 420 | 420 | 0 | 0 | 0 | 0 | 0
J T DEELY 2 |  | CALAVERS_JTD2 | BEXAR | COAL | SOUTH | 1978 | 420 | 420 | 420 | 420 | 420 | 0 | 0 | 0 | 0 | 0
LIMESTONE 1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 831 | 831 | 831 | 831 | 831 | 831 | 831 | 831 | 831 | 831
LIMESTONE 2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 858 | 858 | 858 | 858 | 858 | 858 | 858 | 858 | 858 | 858
MARTIN LAKE 1 |  | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800
MARTIN LAKE 2 |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 805 | 805 | 805 | 805 | 805 | 805 | 805 | 805 | 805 | 805
MONTICELLO 3 |  | MNSES_UNIT3 | TITUS | COAL | NORTH | 1978 | 795 | 795 | 795 | 795 | 795 | 795 | 795 | 795 | 795 | 795
OAK GROVE SES UNIT 1 |  | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 840 | 840 | 840 | 840 | 840 | 840 | 840 | 840 | 840 | 840
OAK GROVE SES UNIT 2 |  | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 825 | 825 | 825 | 825 | 825 | 825 | 825 | 825 | 825 | 825
OKLAUNION 1 |  | OKLA_OKLA_G1 | WILBARGER | COAL | WEST | 1986 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650
SAN MIGUEL 1 |  | SANMIGL_SANMIGG1 | ATASCOSA | COAL | SOUTH | 1982 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391
SANDOW 5 |  | SD5SES_UNIT5 | MILAM | COAL | SOUTH | 2010 | 570 | 570 | 570 | 570 | 570 | 570 | 570 | 570 | 570 | 570
TWIN OAKS 1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156
TWIN OAKS 2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156
W A PARISH 5 |  | WAP_WAP_G5 | FORT BEND | COAL | HOUSTON | 1977 | 659 | 659 | 659 | 659 | 659 | 659 | 659 | 659 | 659 | 659
W A PARISH 6 |  | WAP_WAP_G6 | FORT BEND | COAL | HOUSTON | 1978 | 658 | 658 | 658 | 658 | 658 | 658 | 658 | 658 | 658 | 658
W A PARISH 7 |  | WAP_WAP_G7 | FORT BEND | COAL | HOUSTON | 1980 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577
W A PARISH 8 |  | WAP_WAP_G8 | FORT BEND | COAL | HOUSTON | 1982 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610
SANDY CREEK 1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 970 | 970 | 970 | 970 | 970 | 970 | 970 | 970 | 970 | 970
A VON ROSENBERG 1-CT1 |  | BRAUNIG_AVR1_CT1 | BEXAR | GAS | SOUTH | 2000 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
A VON ROSENBERG 1-CT2 |  | BRAUNIG_AVR1_CT2 | BEXAR | GAS | SOUTH | 2000 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
A VON ROSENBERG 1-ST1 |  | BRAUNIG_AVR1_ST | BEXAR | GAS | SOUTH | 2000 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
ATKINS 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS | NORTH | 1973 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
B M DAVIS 1 |  | B_DAVIS_B_DAVIG1 | NUECES | GAS | SOUTH | 1974 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335
B M DAVIS 2 |  | B_DAVIS_B_DAVIG2 | NUECES | GAS | SOUTH | 1976 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
B M DAVIS 3 |  | B_DAVIS_B_DAVIG3 | NUECES | GAS | SOUTH | 2010 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
B M DAVIS 4 |  | B_DAVIS_B_DAVIG4 | NUECES | GAS | SOUTH | 2010 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
BASTROP ENERGY CENTER 1 |  | BASTEN_GTG1100 | BASTROP | GAS | SOUTH | 2002 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
BASTROP ENERGY CENTER 2 |  | BASTEN_GTG2100 | BASTROP | GAS | SOUTH | 2002 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
BASTROP ENERGY CENTER 3 |  | BASTEN_ST0100 | BASTROP | GAS | SOUTH | 2002 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233
BOSQUE COUNTY PEAKING 1 |  | BOSQUESW_BSQSU_1 | BOSQUE | GAS | NORTH | 2000 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2
BOSQUE COUNTY PEAKING 2 |  | BOSQUESW_BSQSU_2 | BOSQUE | GAS | NORTH | 2000 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2
BOSQUE COUNTY PEAKING 3 |  | BOSQUESW_BSQSU_3 | BOSQUE | GAS | NORTH | 2001 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2
BOSQUE COUNTY PEAKING 4 |  | BOSQUESW_BSQSU_4 | BOSQUE | GAS | NORTH | 2001 | 81.4 | 81.4 | 81.4 | 81.4 | 81.4 | 81.4 | 81.4 | 81.4 | 81.4 | 81.4
BOSQUE COUNTY UNIT 5 |  | BOSQUESW_BSQSU_5 | BOSQUE | GAS | NORTH | 2009 | 190.5 | 190.5 | 190.5 | 190.5 | 190.5 | 190.5 | 190.5 | 190.5 | 190.5 | 190.5
BRAZOS VALLEY 1 |  | BVE_UNIT1 | FORT BEND | GAS | HOUSTON | 2003 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166
BRAZOS VALLEY 2 |  | BVE_UNIT2 | FORT BEND | GAS | HOUSTON | 2003 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166
BRAZOS VALLEY 3 |  | BVE_UNIT3 | FORT BEND | GAS | HOUSTON | 2003 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270
CALENERGY (FALCON SEABOARD) 1 |  | FLCNS_UNIT1 | HOWARD | GAS | WEST | 1987 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
CALENERGY (FALCON SEABOARD) 2 |  | FLCNS_UNIT2 | HOWARD | GAS | WEST | 1987 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
CALENERGY (FALCON SEABOARD) 3 |  | FLCNS_UNIT3 | HOWARD | GAS | WEST | 1988 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
CEDAR BAYOU 1 |  | CBY_CBY_G1 | CHAMBERS | GAS | HOUSTON | 1970 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745
CEDAR BAYOU 2 |  | CBY_CBY_G2 | CHAMBERS | GAS | HOUSTON | 1972 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749
CEDAR BAYOU 4 |  | CBY4_CT41 | CHAMBERS | GAS | HOUSTON | 2009 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163
CEDAR BAYOU 5 |  | CBY4_CT42 | CHAMBERS | GAS | HOUSTON | 2009 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163
CEDAR BAYOU 6 |  | CBY4_ST04 | CHAMBERS | GAS | HOUSTON | 2009 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
COLORADO BEND ENERGY CENTER |  | CBEC_GT1 | WHARTON | GAS | HOUSTON | 2007 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76
COLORADO BEND ENERGY CENTER |  | CBEC_GT2 | WHARTON | GAS | HOUSTON | 2007 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
COLORADO BEND ENERGY CENTER |  | CBEC_GT3 | WHARTON | GAS | HOUSTON | 2008 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
COLORADO BEND ENERGY CENTER |  | CBEC_GT4 | WHARTON | GAS | HOUSTON | 2008 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
COLORADO BEND ENERGY CENTER |  | CBEC_STG1 | WHARTON | GAS | HOUSTON | 2007 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103
COLORADO BEND ENERGY CENTER |  | CBEC_STG2 | WHARTON | GAS | HOUSTON | 2008 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106
CVC CHANNELVIEW 1 |  | CVC_CVC_G1 | HARRIS | GAS | HOUSTON | 2008 | 155.4 | 155.4 | 155.4 | 155.4 | 155.4 | 155.4 | 155.4 | 155.4 | 155.4 | 155.4
CVC CHANNELVIEW 2 |  | CVC_CVC_G2 | HARRIS | GAS | HOUSTON | 2008 | 165.1 | 165.1 | 165.1 | 165.1 | 165.1 | 165.1 | 165.1 | 165.1 | 165.1 | 165.1
CVC CHANNELVIEW 3 |  | CVC_CVC_G3 | HARRIS | GAS | HOUSTON | 2008 | 163.9 | 163.9 | 163.9 | 163.9 | 163.9 | 163.9 | 163.9 | 163.9 | 163.9 | 163.9
CVC CHANNELVIEW 5 |  | CVC_CVC_G5 | HARRIS | GAS | HOUSTON | 2008 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2
DANSBY 1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS | NORTH | 1978 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
DANSBY 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS | NORTH | 2004 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
DANSBY 3 |  | DANSBY_DANSBYG3 | BRAZOS | GAS | NORTH | 2010 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
DECKER CREEK 1 |  | DECKER_DPG1 | TRAVIS | GAS | SOUTH | 1971 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315
DECKER CREEK 2 |  | DECKER_DPG2 | TRAVIS | GAS | SOUTH | 1978 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
DECKER CREEK G1 |  | DECKER_DPGT_1 | TRAVIS | GAS | SOUTH | 1989 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
DECKER CREEK G2 |  | DECKER_DPGT_2 | TRAVIS | GAS | SOUTH | 1989 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
DECKER CREEK G3 |  | DECKER_DPGT_3 | TRAVIS | GAS | SOUTH | 1989 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
DECKER CREEK G4 |  | DECKER_DPGT_4 | TRAVIS | GAS | SOUTH | 1989 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
DECORDOVA A |  | DCSES_CT10 | HOOD | GAS | NORTH | 2010 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71
DECORDOVA B |  | DCSES_CT20 | HOOD | GAS | NORTH | 2010 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
DECORDOVA C |  | DCSES_CT30 | HOOD | GAS | NORTH | 2010 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
DECORDOVA D |  | DCSES_CT40 | HOOD | GAS | NORTH | 2010 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
DEER PARK ENERGY CENTER 1 |  | DDPEC_GT1 | HARRIS | GAS | HOUSTON | 2002 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181
DEER PARK ENERGY CENTER 2 |  | DDPEC_GT2 | HARRIS | GAS | HOUSTON | 2002 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193
DEER PARK ENERGY CENTER 3 |  | DDPEC_GT3 | HARRIS | GAS | HOUSTON | 2002 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181
DEER PARK ENERGY CENTER 4 |  | DDPEC_GT4 | HARRIS | GAS | HOUSTON | 2002 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193
DEER PARK ENERGY CENTER S |  | DDPEC_ST1 | HARRIS | GAS | HOUSTON | 2002 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290
ENNIS POWER STATION 1 |  | ETCCS_UNIT1 | ELLIS | GAS | NORTH | 2002 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116
ENNIS POWER STATION 2 |  | ETCCS_CT1 | ELLIS | GAS | NORTH | 2002 | 196 | 196 | 196 | 196 | 196 | 196 | 196 | 196 | 196 | 196
EXTEX LA PORTE PWR STN (AIRPRO) 1 |  | AZ_AZ_G1 | HARRIS | GAS | HOUSTON | 2009 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
EXTEX LA PORTE PWR STN (AIRPRO) 2 |  | AZ_AZ_G2 | HARRIS | GAS | HOUSTON | 2009 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
EXTEX LA PORTE PWR STN (AIRPRO) 3 |  | AZ_AZ_G3 | HARRIS | GAS | HOUSTON | 2009 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
EXTEX LA PORTE PWR STN (AIRPRO) 4 |  | AZ_AZ_G4 | HARRIS | GAS | HOUSTON | 2009 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
FORNEY ENERGY CENTER GT11 |  | FRNYPP_GT11 | KAUFMAN | GAS | NORTH | 2003 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4
FORNEY ENERGY CENTER GT12 |  | FRNYPP_GT12 | KAUFMAN | GAS | NORTH | 2003 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4
FORNEY ENERGY CENTER GT13 |  | FRNYPP_GT13 | KAUFMAN | GAS | NORTH | 2003 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4
FORNEY ENERGY CENTER GT21 |  | FRNYPP_GT21 | KAUFMAN | GAS | NORTH | 2003 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4
FORNEY ENERGY CENTER GT22 |  | FRNYPP_GT22 | KAUFMAN | GAS | NORTH | 2003 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4
FORNEY ENERGY CENTER GT23 |  | FRNYPP_GT23 | KAUFMAN | GAS | NORTH | 2003 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4 | 168.4
FORNEY ENERGY CENTER STG10 |  | FRNYPP_ST10 | KAUFMAN | GAS | NORTH | 2003 | 401.2 | 401.2 | 401.2 | 401.2 | 401.2 | 401.2 | 401.2 | 401.2 | 401.2 | 401.2
FORNEY ENERGY CENTER STG20 |  | FRNYPP_ST20 | KAUFMAN | GAS | NORTH | 2003 | 401.2 | 401.2 | 401.2 | 401.2 | 401.2 | 401.2 | 401.2 | 401.2 | 401.2 | 401.2
FREESTONE ENERGY CENTER 1 |  | FREC_GT1 | FREESTONE | GAS | NORTH | 2002 | 151.56 | 151.56 | 151.56 | 151.56 | 151.56 | 151.56 | 151.56 | 151.56 | 151.56 | 151.56
FREESTONE ENERGY CENTER 2 |  | FREC_GT2 | FREESTONE | GAS | NORTH | 2002 | 151.56 | 151.56 | 151.56 | 151.56 | 151.56 | 151.56 | 151.56 | 151.56 | 151.56 | 151.56
FREESTONE ENERGY CENTER 3 |  | FREC_ST3 | FREESTONE | GAS | NORTH | 2002 | 176.23 | 176.23 | 176.23 | 176.23 | 176.23 | 176.23 | 176.23 | 176.23 | 176.23 | 176.23
FREESTONE ENERGY CENTER 4 |  | FREC_GT4 | FREESTONE | GAS | NORTH | 2002 | 151.69 | 151.69 | 151.69 | 151.69 | 151.69 | 151.69 | 151.69 | 151.69 | 151.69 | 151.69
FREESTONE ENERGY CENTER 5 |  | FREC_GT5 | FREESTONE | GAS | NORTH | 2002 | 151.69 | 151.69 | 151.69 | 151.69 | 151.69 | 151.69 | 151.69 | 151.69 | 151.69 | 151.69
FREESTONE ENERGY CENTER 6 |  | FREC_ST6 | FREESTONE | GAS | NORTH | 2002 | 174.47 | 174.47 | 174.47 | 174.47 | 174.47 | 174.47 | 174.47 | 174.47 | 174.47 | 174.47
FRONTERA 1 |  | FRONTERA_FRONTEG1 | HILDALGO | GAS | SOUTH | 1999 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
FRONTERA 2 |  | FRONTERA_FRONTEG2 | HILDALGO | GAS | SOUTH | 1999 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
FRONTERA 3 |  | FRONTERA_FRONTEG3 | HILDALGO | GAS | SOUTH | 2000 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
GRAHAM 1 |  | GRSES_UNIT1 | YOUNG | GAS | WEST | 1960 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225
GRAHAM 2 |  | GRSES_UNIT2 | YOUNG | GAS | WEST | 1969 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390
GREENS BAYOU 5 |  | GBY_GBY_5 | HARRIS | GAS | HOUSTON | 1973 | 406 | 406 | 406 | 406 | 406 | 406 | 406 | 406 | 406 | 406
GREENS BAYOU 73 |  | GBY_GBYGT73 | HARRIS | GAS | HOUSTON | 1976 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
GREENS BAYOU 74 |  | GBY_GBYGT74 | HARRIS | GAS | HOUSTON | 1976 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
GREENS BAYOU 81 |  | GBY_GBYGT81 | HARRIS | GAS | HOUSTON | 1976 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
GREENS BAYOU 83 |  | GBY_GBYGT83 | HARRIS | GAS | HOUSTON | 1976 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
GREENS BAYOU 84 |  | GBY_GBYGT84 | HARRIS | GAS | HOUSTON | 1976 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58
GREENVILLE ENGINE PLANT |  | STEAM_ENGINE_1 | HUNT | GAS | NORTH | 2010 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439
GREENVILLE ENGINE PLANT |  | STEAM_ENGINE_2 | HUNT | GAS | NORTH | 2010 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439
GREENVILLE ENGINE PLANT |  | STEAM_ENGINE_3 | HUNT | GAS | NORTH | 2010 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439
GUADALUPE GEN STN 1 |  | GUADG_GAS1 | GUADALUPE | GAS | SOUTH | 2000 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148
GUADALUPE GEN STN 2 |  | GUADG_GAS2 | GUADALUPE | GAS | SOUTH | 2000 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148
GUADALUPE GEN STN 3 |  | GUADG_GAS3 | GUADALUPE | GAS | SOUTH | 2000 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148
GUADALUPE GEN STN 4 |  | GUADG_GAS4 | GUADALUPE | GAS | SOUTH | 2000 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148
GUADALUPE GEN STN 5 |  | GUADG_STM5 | GUADALUPE | GAS | SOUTH | 2000 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197
GUADALUPE GEN STN 6 |  | GUADG_STM6 | GUADALUPE | GAS | SOUTH | 2000 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197
HANDLEY 3 |  | HLSES_UNIT3 | TARRANT | GAS | NORTH | 1963 | 395 | 395 | 395 | 395 | 395 | 395 | 395 | 395 | 395 | 395
HANDLEY 4 |  | HLSES_UNIT4 | TARRANT | GAS | NORTH | 1976 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435
HANDLEY 5 |  | HLSES_UNIT5 | TARRANT | GAS | NORTH | 1977 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435
HAYS ENERGY FACILITY 1 |  | HAYSEN_HAYSENG1 | HAYS | GAS | SOUTH | 2002 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216
HAYS ENERGY FACILITY 2 |  | HAYSEN_HAYSENG2 | HAYS | GAS | SOUTH | 2002 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216
HAYS ENERGY FACILITY 3 |  | HAYSEN_HAYSENG3 | HAYS | GAS | SOUTH | 2002 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225
HAYS ENERGY FACILITY 4 |  | HAYSEN_HAYSENG4 | HAYS | GAS | SOUTH | 2002 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225
HIDALGO 1 |  | DUKE_DUKE_GT1 | HILDALGO | GAS | SOUTH | 2000 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143
HIDALGO 2 |  | DUKE_DUKE_GT2 | HILDALGO | GAS | SOUTH | 2000 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143
HIDALGO 3 |  | DUKE_DUKE_ST1 | HILDALGO | GAS | SOUTH | 2000 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172
JACK COUNTY GENFACILITY 2 |  | JCKCNTY2_CT3 | JACK | GAS | NORTH | 2011 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166
JACK COUNTY GENFACILITY 2 |  | JCKCNTY2_CT4 | JACK | GAS | NORTH | 2011 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
JACK COUNTY GENFACILITY 2 |  | JCKCNTY2_ST2 | JACK | GAS | NORTH | 2011 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295
JACK COUNTY GENFACILITY 1 |  | JACKCNTY_CT1 | JACK | GAS | NORTH | 2005 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166
JACK COUNTY GENFACILITY 1 |  | JACKCNTY_CT2 | JACK | GAS | NORTH | 2005 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
JACK COUNTY GENFACILITY 1 |  | JACKCNTY_STG | JACK | GAS | NORTH | 2005 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295
JOHNSON COUNTY GENFACILITY 1 |  | TEN_CT1 | JOHNSON | GAS | NORTH | 1997 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163
JOHNSON COUNTY GENFACILITY 2 |  | TEN_STG | JOHNSON | GAS | NORTH | 1997 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106
LAKE HUBBARD 1 |  | LHSES_UNIT1 | DALLAS | GAS | NORTH | 1970 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392
LAKE HUBBARD 2 |  | LH2SES_UNIT2 | DALLAS | GAS | NORTH | 2011 | 515 | 515 | 515 | 515 | 515 | 515 | 515 | 515 | 515 | 515
LAMAR POWER PROJECT CT11 |  | LPCCS_CT11 | LAMAR | GAS | NORTH | 2000 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8
LAMAR POWER PROJECT CT12 |  | LPCCS_CT12 | LAMAR | GAS | NORTH | 2000 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8
LAMAR POWER PROJECT CT21 |  | LPCCS_CT21 | LAMAR | GAS | NORTH | 2000 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8
LAMAR POWER PROJECT CT22 |  | LPCCS_CT22 | LAMAR | GAS | NORTH | 2000 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8 | 153.8
LAMAR POWER PROJECT STG1 |  | LPCCS_UNIT1 | LAMAR | GAS | NORTH | 2000 | 193.4 | 193.4 | 193.4 | 193.4 | 193.4 | 193.4 | 193.4 | 193.4 | 193.4 | 193.4
LAMAR POWER PROJECT STG2 |  | LPCCS_UNIT2 | LAMAR | GAS | NORTH | 2000 | 193.4 | 193.4 | 193.4 | 193.4 | 193.4 | 193.4 | 193.4 | 193.4 | 193.4 | 193.4
LAREDO PEAKING 4 |  | LARDVFTN_G4 | WEBB | GAS | SOUTH | 2008 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2
LAREDO PEAKING 5 |  | LARDVFTN_G5 | WEBB | GAS | SOUTH | 2008 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2
LEON CREEK PEAKING 1 |  | LEON_CRK_LCPCT1 | BEXAR | GAS | SOUTH | 2004 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
LEON CREEK PEAKING 2 |  | LEON_CRK_LCPCT2 | BEXAR | GAS | SOUTH | 2004 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
LEON CREEK PEAKING 3 |  | LEON_CRK_LCPCT3 | BEXAR | GAS | SOUTH | 2004 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
LEON CREEK PEAKING 4 |  | LEON_CRK_LCPCT4 | BEXAR | GAS | SOUTH | 2004 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
LOST PINES 1 |  | LOSTPI_LOSTPGT1 | BASTROP | GAS | SOUTH | 2001 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170
LOST PINES 2 |  | LOSTPI_LOSTPGT2 | BASTROP | GAS | SOUTH | 2001 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170
LOST PINES 3 |  | LOSTPI_LOSTPST1 | BASTROP | GAS | SOUTH | 2001 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188
MAGIC VALLEY 1 |  | NEDIN_NEDIN_G1 | HIDALGO | GAS | SOUTH | 2001 | 208.58 | 208.58 | 208.58 | 208.58 | 208.58 | 208.58 | 208.58 | 208.58 | 208.58 | 208.58
MAGIC VALLEY 2 |  | NEDIN_NEDIN_G2 | HIDALGO | GAS | SOUTH | 2001 | 208.58 | 208.58 | 208.58 | 208.58 | 208.58 | 208.58 | 208.58 | 208.58 | 208.58 | 208.58
MAGIC VALLEY 3 |  | NEDIN_NEDIN_G3 | HIDALGO | GAS | SOUTH | 2001 | 252.98 | 252.98 | 252.98 | 252.98 | 252.98 | 252.98 | 252.98 | 252.98 | 252.98 | 252.98
MIDLOTHIAN 1 |  | MDANP_CT1 | ELLIS | GAS | NORTH | 2001 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216
MIDLOTHIAN 2 |  | MDANP_CT2 | ELLIS | GAS | NORTH | 2001 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216
MIDLOTHIAN 3 |  | MDANP_CT3 | ELLIS | GAS | NORTH | 2001 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216
MIDLOTHIAN 4 |  | MDANP_CT4 | ELLIS | GAS | NORTH | 2001 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216
MIDLOTHIAN 5 |  | MDANP_CT5 | ELLIS | GAS | NORTH | 2002 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225
MIDLOTHIAN 6 |  | MDANP_CT6 | ELLIS | GAS | NORTH | 2002 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225
MORGAN CREEK A |  | MGSES_CT1 | MITCHELL | GAS | WEST | 1988 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
MORGAN CREEK B |  | MGSES_CT2 | MITCHELL | GAS | WEST | 1988 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
MORGAN CREEK C |  | MGSES_CT3 | MITCHELL | GAS | WEST | 1988 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
MORGAN CREEK D |  | MGSES_CT4 | MITCHELL | GAS | WEST | 1988 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
MORGAN CREEK E |  | MGSES_CT5 | MITCHELL | GAS | WEST | 1988 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
MORGAN CREEK F |  | MGSES_CT6 | MITCHELL | GAS | WEST | 1988 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67
MOUNTAIN CREEK 6 |  | MCSES_UNIT6 | DALLAS | GAS | NORTH | 1956 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
MOUNTAIN CREEK 7 |  | MCSES_UNIT7 | DALLAS | GAS | NORTH | 1958 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115
MOUNTAIN CREEK 8 |  | MCSES_UNIT8 | DALLAS | GAS | NORTH | 1967 | 565 | 565 | 565 | 565 | 565 | 565 | 565 | 565 | 565 | 565
NUECES BAY 7 |  | NUECES_B_NUECESG7 | NUECES | GAS | SOUTH | 1972 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319 | 319
NUECES BAY 8 |  | NUECES_B_NUECESG8 | NUECES | GAS | SOUTH | 2010 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
NUECES BAY 9 |  | NUECES_B_NUECESG9 | NUECES | GAS | SOUTH | 2010 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
O W SOMMERS 1 |  | CALAVERS_OWS1 | BEXAR | GAS | SOUTH | 1972 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
O W SOMMERS 2 |  | CALAVERS_OWS2 | BEXAR | GAS | SOUTH | 1974 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
ODESSA-ECTOR GEN STN C11 |  | OECCS_CT11 | ECTOR | GAS | WEST | 2001 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151
ODESSA-ECTOR GEN STN C12 |  | OECCS_CT12 | ECTOR | GAS | WEST | 2001 | 140.4 | 140.4 | 140.4 | 140.4 | 140.4 | 140.4 | 140.4 | 140.4 | 140.4 | 140.4
ODESSA-ECTOR GEN STN C21 |  | OECCS_CT21 | ECTOR | GAS | WEST | 2001 | 144.7 | 144.7 | 144.7 | 144.7 | 144.7 | 144.7 | 144.7 | 144.7 | 144.7 | 144.7
ODESSA-ECTOR GEN STN C22 |  | OECCS_CT22 | ECTOR | GAS | WEST | 2001 | 142.4 | 142.4 | 142.4 | 142.4 | 142.4 | 142.4 | 142.4 | 142.4 | 142.4 | 142.4
ODESSA-ECTOR GEN STN ST1 |  | OECCS_UNIT1 | ECTOR | GAS | WEST | 2001 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210
ODESSA-ECTOR GEN STN ST2 |  | OECCS_UNIT2 | ECTOR | GAS | WEST | 2001 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210
PARIS ENERGY CENTER 1 |  | TNSKA_GT1 | LAMAR | GAS | NORTH | 1989 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76
PARIS ENERGY CENTER 2 |  | TNSKA_GT2 | LAMAR | GAS | NORTH | 1989 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76
PARIS ENERGY CENTER 3 |  | TNSKA_STG | LAMAR | GAS | NORTH | 1990 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87
PASGEN |  | PSG_PSG_GT2 | HARRIS | GAS | HOUSTON | 2000 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164
PASGEN |  | PSG_PSG_GT3 | HARRIS | GAS | HOUSTON | 2000 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164
PASGEN |  | PSG_PSG_ST2 | HARRIS | GAS | HOUSTON | 2000 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
PEARSALL 1 |  | PEARSALL_PEARS_1 | FRIO | GAS | SOUTH | 1961 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
PEARSALL 2 |  | PEARSALL_PEARS_2 | FRIO | GAS | SOUTH | 1961 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
PEARSALL 3 |  | PEARSALL_PEARS_3 | FRIO | GAS | SOUTH | 1961 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
PEARSALL ENGINE PLANT |  | PEARSAL2_AGR_A | FRIO | GAS | SOUTH | 2012 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64
PEARSALL ENGINE PLANT |  | PEARSAL2_AGR_B | FRIO | GAS | SOUTH | 2012 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64
PEARSALL ENGINE PLANT |  | PEARSAL2_AGR_C | FRIO | GAS | SOUTH | 2012 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64
PEARSALL ENGINE PLANT |  | PEARSAL2_AGR_D | FRIO | GAS | SOUTH | 2012 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64
PERMIAN BASIN A |  | PB2SES_CT1 | WARD | GAS | WEST | 1988 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
PERMIAN BASIN B |  | PB2SES_CT2 | WARD | GAS | WEST | 1988 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
PERMIAN BASIN C |  | PB2SES_CT3 | WARD | GAS | WEST | 1988 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
PERMIAN BASIN D |  | PB2SES_CT4 | WARD | GAS | WEST | 1990 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
PERMIAN BASIN E |  | PB2SES_CT5 | WARD | GAS | WEST | 1990 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
POWERLANE PLANT 1 |  | STEAM1A_STEAM_1 | HUNT | GAS | NORTH | 2009 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
POWERLANE PLANT 2 |  | STEAM_STEAM_2 | HUNT | GAS | NORTH | 1967 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
POWERLANE PLANT 3 |  | STEAM_STEAM_3 | HUNT | GAS | NORTH | 1978 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41
QUAIL RUN ENERGY GT1 |  | QALSW_GT2 | ECTOR | GAS | WEST | 2007 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
QUAIL RUN ENERGY GT2 |  | QALSW_GT3 | ECTOR | GAS | WEST | 2008 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
QUAIL RUN ENERGY GT3 |  | QALSW_STG1 | ECTOR | GAS | WEST | 2007 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
QUAIL RUN ENERGY GT4 |  | QALSW_STG2 | ECTOR | GAS | WEST | 2008 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
QUAIL RUN ENERGY STG1 |  | QALSW_GT1 | ECTOR | GAS | WEST | 2007 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
QUAIL RUN ENERGY STG2 |  | QALSW_GT4 | ECTOR | GAS | WEST | 2008 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
R W MILLER 1 |  | MIL_MILLERG1 | PALO PINTO | GAS | NORTH | 2000 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
R W MILLER 2 |  | MIL_MILLERG2 | PALO PINTO | GAS | NORTH | 2000 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
R W MILLER 3 |  | MIL_MILLERG3 | PALO PINTO | GAS | NORTH | 2000 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208
R W MILLER 4 |  | MIL_MILLERG4 | PALO PINTO | GAS | NORTH | 2000 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104
R W MILLER 5 |  | MIL_MILLERG5 | PALO PINTO | GAS | NORTH | 2000 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104
RAY OLINGER 1 |  | OLINGR_OLING_1 | COLLIN | GAS | NORTH | 1967 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
RAY OLINGER 2 |  | OLINGR_OLING_2 | COLLIN | GAS | NORTH | 1971 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107
RAY OLINGER 3 |  | OLINGR_OLING_3 | COLLIN | GAS | NORTH | 1975 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146
RAY OLINGER 4 |  | OLINGR_OLING_4 | COLLIN | GAS | NORTH | 2001 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
RAYBURN 1 |  | RAYBURN_RAYBURG1 | VICTORIA | GAS | SOUTH | 1963 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
RAYBURN 10 |  | RAYBURN_RAYBURG10 | VICTORIA | GAS | SOUTH | 2003 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
RAYBURN 2 |  | RAYBURN_RAYBURG2 | VICTORIA | GAS | SOUTH | 1963 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
RAYBURN 7 |  | RAYBURN_RAYBURG7 | VICTORIA | GAS | SOUTH | 2003 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
RAYBURN 8 |  | RAYBURN_RAYBURG8 | VICTORIA | GAS | SOUTH | 2003 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
RAYBURN 9 |  | RAYBURN_RAYBURG9 | VICTORIA | GAS | SOUTH | 2003 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
RIO NOGALES 1 |  | RIONOG_CT1 | GUADALUPE | GAS | SOUTH | 2002 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154
RIO NOGALES 2 |  | RIONOG_CT2 | GUADALUPE | GAS | SOUTH | 2002 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154
RIO NOGALES 3 |  | RIONOG_CT3 | GUADALUPE | GAS | SOUTH | 2002 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154
RIO NOGALES 4 |  | RIONOG_ST1 | GUADALUPE | GAS | SOUTH | 2002 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323
SAN JACINTO SES 1 |  | SJS_SJS_G1 | HARRIS | GAS | HOUSTON | 1995 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
SAN JACINTO SES 2 |  | SJS_SJS_G2 | HARRIS | GAS | HOUSTON | 1995 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
SANDHILL ENERGY CENTER 1 |  | SANDHSYD_SH1 | TRAVIS | GAS | SOUTH | 2001 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
SANDHILL ENERGY CENTER 2 |  | SANDHSYD_SH2 | TRAVIS | GAS | SOUTH | 2001 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
SANDHILL ENERGY CENTER 3 |  | SANDHSYD_SH3 | TRAVIS | GAS | SOUTH | 2001 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
SANDHILL ENERGY CENTER 4 |  | SANDHSYD_SH4 | TRAVIS | GAS | SOUTH | 2001 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
SANDHILL ENERGY CENTER 5A |  | SANDHSYD_SH_5A | TRAVIS | GAS | SOUTH | 2004 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SANDHILL ENERGY CENTER 5C |  | SANDHSYD_SH_5C | TRAVIS | GAS | SOUTH | 2004 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
SANDHILL ENERGY CENTER 6 |  | SANDHSYD_SH6 | TRAVIS | GAS | SOUTH | 2010 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
SANDHILL ENERGY CENTER 7 |  | SANDHSYD_SH7 | TRAVIS | GAS | SOUTH | 2010 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
SILAS RAY 10 |  | SILASRAY_SILAS_10 | CAMERON | GAS | SOUTH | 2004 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
SILAS RAY 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS | SOUTH | 1962 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
SILAS RAY 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS | SOUTH | 1996 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
SIM GIDEON 1 |  | GIDEON_GIDEONG1 | BASTROP | GAS | SOUTH | 1965 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130
SIM GIDEON 2 |  | GIDEON_GIDEONG2 | BASTROP | GAS | SOUTH | 1968 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135
SIM GIDEON 3 |  | GIDEON_GIDEONG3 | BASTROP | GAS | SOUTH | 1972 | 332 | 332 | 332 | 332 | 332 | 332 | 332 | 332 | 332 | 332
SPENCER 4 |  | SPNCER_SPNCE_4 | DENTON | GAS | NORTH | 1966 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
SPENCER 5 |  | SPNCER_SPNCE_5 | DENTON | GAS | NORTH | 1973 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
STRYKER CREEK 1 |  | SCSES_UNIT1A | CHEROKEE | GAS | NORTH | 1958 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
STRYKER CREEK 2 |  | SCSES_UNIT2 | CHEROKEE | GAS | NORTH | 1965 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502
T H WHARTON 3 |  | THW_THWST_3 | HARRIS | GAS | HOUSTON | 1974 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104
T H WHARTON 31 |  | THW_THWGT31 | HARRIS | GAS | HOUSTON | 1972 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON 32 |  | THW_THWGT32 | HARRIS | GAS | HOUSTON | 1972 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON 33 |  | THW_THWGT33 | HARRIS | GAS | HOUSTON | 1972 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON 34 |  | THW_THWGT34 | HARRIS | GAS | HOUSTON | 1972 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON 4 |  | THW_THWST_4 | HARRIS | GAS | HOUSTON | 1974 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104
T H WHARTON 41 |  | THW_THWGT41 | HARRIS | GAS | HOUSTON | 1972 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON 42 |  | THW_THWGT42 | HARRIS | GAS | HOUSTON | 1972 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON 43 |  | THW_THWGT43 | HARRIS | GAS | HOUSTON | 1974 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON 44 |  | THW_THWGT44 | HARRIS | GAS | HOUSTON | 1974 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON 51 |  | THW_THWGT51 | HARRIS | GAS | HOUSTON | 1975 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON 52 |  | THW_THWGT52 | HARRIS | GAS | HOUSTON | 1975 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON 53 |  | THW_THWGT53 | HARRIS | GAS | HOUSTON | 1975 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON 54 |  | THW_THWGT54 | HARRIS | GAS | HOUSTON | 1975 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON 55 |  | THW_THWGT55 | HARRIS | GAS | HOUSTON | 1975 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON 56 |  | THW_THWGT56 | HARRIS | GAS | HOUSTON | 1975 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON G1 |  | THW_THWGT_1 | HARRIS | GAS | HOUSTON | 1967 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
TEXAS CITY 1 |  | TXCTY_CTA | GALVESTON | GAS | HOUSTON | 2000 | 96.58 | 96.58 | 96.58 | 96.58 | 96.58 | 96.58 | 96.58 | 96.58 | 96.58 | 96.58
TEXAS CITY 2 |  | TXCTY_CTB | GALVESTON | GAS | HOUSTON | 2000 | 96.58 | 96.58 | 96.58 | 96.58 | 96.58 | 96.58 | 96.58 | 96.58 | 96.58 | 96.58
TEXAS CITY 3 |  | TXCTY_CTC | GALVESTON | GAS | HOUSTON | 2000 | 96.58 | 96.58 | 96.58 | 96.58 | 96.58 | 96.58 | 96.58 | 96.58 | 96.58 | 96.58
TEXAS CITY 4 |  | TXCTY_ST | GALVESTON | GAS | HOUSTON | 2000 | 131.58 | 131.58 | 131.58 | 131.58 | 131.58 | 131.58 | 131.58 | 131.58 | 131.58 | 131.58
TEXAS GULF SULPHUR |  | TGF_TGFGT_1 | WHARTON | GAS | HOUSTON | 1985 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
TRINIDAD 6 |  | TRSES_UNIT6 | HENDERSON | GAS | NORTH | 2011 | 226 | 226 | 226 | 226 | 226 | 226 | 226 | 226 | 226 | 226
V H BRAUNIG 1 |  | BRAUNIG_VHB1 | BEXAR | GAS | SOUTH | 1966 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
V H BRAUNIG 2 |  | BRAUNIG_VHB2 | BEXAR | GAS | SOUTH | 1968 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230
V H BRAUNIG 3 |  | BRAUNIG_VHB3 | BEXAR | GAS | SOUTH | 1970 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412
V H BRAUNIG 5 |  | BRAUNIG_VHB6CT5 | BEXAR | GAS | SOUTH | 2009 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
V H BRAUNIG 6 |  | BRAUNIG_VHB6CT6 | BEXAR | GAS | SOUTH | 2009 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
V H BRAUNIG 7 |  | BRAUNIG_VHB6CT7 | BEXAR | GAS | SOUTH | 2009 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
V H BRAUNIG 8 |  | BRAUNIG_VHB6CT8 | BEXAR | GAS | SOUTH | 2009 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
VICTORIA POWER STATION 5 |  | VICTORIA_VICTORG5 | VICTORIA | GAS | SOUTH | 2009 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
VICTORIA POWER STATION 6 |  | VICTORIA_VICTORG6 | VICTORIA | GAS | SOUTH | 2009 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
W A PARISH 1 |  | WAP_WAP_G1 | FORT BEND | GAS | HOUSTON | 1958 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
W A PARISH 2 |  | WAP_WAP_G2 | FORT BEND | GAS | HOUSTON | 1958 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
W A PARISH 3 |  | WAP_WAP_G3 | FORT BEND | GAS | HOUSTON | 1961 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258
W A PARISH 4 |  | WAP_WAP_G4 | FORT BEND | GAS | HOUSTON | 1968 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552
W A PARISH T1 |  | WAP_WAPGT_1 | FORT BEND | GAS | HOUSTON | 1967 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
WICHITA FALLS 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS | WEST | 1987 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
WICHITA FALLS 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS | WEST | 1987 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
WICHITA FALLS 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS | WEST | 1987 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
WICHITA FALLS 4 |  | WFCOGEN_UNIT4 | WICHITA | GAS | WEST | 1987 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
WINCHESTER POWER PARK 1 |  | WIPOPA_WPP_G1 | FAYETTE | GAS | SOUTH | 2009 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
WINCHESTER POWER PARK 2 |  | WIPOPA_WPP_G2 | FAYETTE | GAS | SOUTH | 2009 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
WINCHESTER POWER PARK 3 |  | WIPOPA_WPP_G3 | FAYETTE | GAS | SOUTH | 2009 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
WINCHESTER POWER PARK 4 |  | WIPOPA_WPP_G4 | FAYETTE | GAS | SOUTH | 2009 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
WISE-TRACTEBEL POWER PROJ. 1 |  | WCPP_CT1 | WISE | GAS | NORTH | 2004 | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212
WISE-TRACTEBEL POWER PROJ. 2 |  | WCPP_CT2 | WISE | GAS | NORTH | 2004 | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 212
WISE-TRACTEBEL POWER PROJ. 3 |  | WCPP_ST1 | WISE | GAS | NORTH | 2004 | 241 | 241 | 241 | 241 | 241 | 241 | 241 | 241 | 241 | 241
WOLF HOLLOW POWER PROJ. 1 |  | WHCCS_CT1 | HOOD | GAS | NORTH | 2002 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5
WOLF HOLLOW POWER PROJ. 2 |  | WHCCS_CT2 | HOOD | GAS | NORTH | 2002 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5
WOLF HOLLOW POWER PROJ. 3 |  | WHCCS_STG | HOOD | GAS | NORTH | 2002 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280
PETRO NOVA - WA PARISH |  | PNPI_GT2 | FORT BEND | GAS | HOUSTON | 2013 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
COMANCHE PEAK 1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1205 | 1205 | 1205 | 1205 | 1205 | 1205 | 1205 | 1205 | 1205 | 1205
COMANCHE PEAK 2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1195 | 1195 | 1195 | 1195 | 1195 | 1195 | 1195 | 1195 | 1195 | 1195
SOUTH TEXAS 1 |  | STP_STP_G1 | MATAGORDA | NUCLEAR | SOUTH | 1988 | 1375 | 1375 | 1375 | 1375 | 1375 | 1375 | 1375 | 1375 | 1375 | 1375
SOUTH TEXAS 2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | SOUTH | 1989 | 1375 | 1375 | 1375 | 1375 | 1375 | 1375 | 1375 | 1375 | 1375 | 1375
NOTREES BATTERY |  | NWF_NBS | WINKLER/ECTOR | STORAGE | WEST | 2012 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7
AES DEEPWATER |  | APD_APD_PS1 | HARRIS | STORAGE | HOUSTON | 2010 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
WEBBERVILLE |  | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5
ACACIA SOLAR |  | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 9.99 | 9.99 | 9.99 | 9.99 | 9.99 | 9.99 | 9.99 | 9.99 | 9.99 | 9.99
OCI ALAMO 1 | 13INR0058 | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.183 | 39.183 | 39.183 | 39.183 | 39.183 | 39.183 | 39.183 | 39.183 | 39.183 | 39.183
BLUE WING 1 |  | DG_BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.56 | 7.56 | 7.56 | 7.56 | 7.56 | 7.56 | 7.56 | 7.56 | 7.56 | 7.56
BLUE WING 2 |  | DG_ELMEN_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3
SOMERSET 1 |  | DG_SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61
SOMERSET 2 |  | DG_SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
SUNEDISON RABEL ROAD |  | DG_VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SUNEDISON VALLEY ROAD |  | DG_VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
NACOGDOCHES POWER |  | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105
LUFKIN BIOMASS |  | LFBIO_UNIT1 | ANGELINA | BIOMASS | NORTH | 2012 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
ALVIN |  | AV_DG1 | GALVESTON | BIOMASS | HOUSTON | 2002 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
AUSTIN LANDFILL GAS |  | DG_SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
COVEL GARDENS POWER STATION |  | DG_MEDIN_1UNIT | BEXAR | BIOMASS | SOUTH | 2005 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
DFW GAS RECOVERY |  | DG_BIO2_4UNITS | DENTON | BIOMASS | NORTH | 2009 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
DG_BIOENERGY PARTNERS |  | DG_BIOE_2UNITS | DENTON | BIOMASS | NORTH | 1988 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2
FW REGION GEN FACILITY |  | DG_RDLML_1UNIT | TARRANT | BIOMASS | NORTH | 2011 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
HUMBLE |  | HB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
LIBERTY |  | LB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 3.872 | 3.872 | 3.872 | 3.872 | 3.872 | 3.872 | 3.872 | 3.872 | 3.872 | 3.872
MCKINNEY LANDFILL |  | DG_MKNSW_2UNITS | COLLIN | BIOMASS | NORTH | 2011 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
MESQUITE CREEK ENERGY |  | DG_FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
SKYLINE LANDFILL GAS |  | DG_FERIS_4_UNITS | DALLAS | BIOMASS | NORTH | 2007 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
TRINITY BAY |  | TRN_DG1 | CHAMBERS | BIOMASS | HOUSTON | 2002 | 3.872 | 3.872 | 3.872 | 3.872 | 3.872 | 3.872 | 3.872 | 3.872 | 3.872 | 3.872
TRINITY OAKS LFG |  | DG_KLBRG_1UNIT | DALLAS | BIOMASS | NORTH | 2011 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
WALZEM ROAD |  | DG_WALZE_4UNITS | BEXAR | BIOMASS | SOUTH | 2002 | 9.78 | 9.78 | 9.78 | 9.78 | 9.78 | 9.78 | 9.78 | 9.78 | 9.78 | 9.78
WESTSIDE |  | DG_WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
KMAYBTO |  | DG_KMASB_1UNIT | WICHITA | BIOMASS | WEST | 2011 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125
Operational Capacity Total (Coal, Gas, Nuclear, Biomass, Solar) | [6 empty] | 62668.329 | 62668.329 | 62668.329 | 62668.329 | 62668.329 | 61828.329 | 61828.329 | 61828.329 | 61828.329 | 61828.329
Operational Resources (Hydro)
CANYON |  | CANYHY_CANYHYG1 | COMAL |  | SOUTH | 1989 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
EAGLE PASS HYDRO |  | EAGLE_HY_EAGLE_HY1 | MAVERICK |  | SOUTH | 2005 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
LAKEWOOD TAP |  | DG_LKWDT_2UNITS | GONZALES |  | SOUTH | 1931 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
LEWISVILLE |  | DG_LWSVL_1UNIT | DENTON |  | NORTH | 1991 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2
MCQUEENEY |  | DG_MCQUE_5UNITS | GUADALUPE |  | SOUTH | 1928 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7
SCHUMANSVILLE |  | DG_SCHUM_2UNITS | GUADALUPE |  | SOUTH | 1928 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6
AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE |  | SOUTH | 1983 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9
AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE |  | SOUTH | 1983 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9
AUSTIN 1 |  | AUSTPL_AUSTING1 | TRAVIS |  | SOUTH | 1940 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
AUSTIN 2 |  | AUSTPL_AUSTING2 | TRAVIS |  | SOUTH | 1940 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
BUCHANAN 1 |  | BUCHAN_BUCHANG1 | LLANO |  | SOUTH | 1938 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
BUCHANAN 2 |  | BUCHAN_BUCHANG2 | LLANO |  | SOUTH | 1938 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
BUCHANAN 3 |  | BUCHAN_BUCHANG3 | LLANO |  | SOUTH | 1950 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON |  | NORTH | 1944 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON |  | NORTH | 1948 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR |  | SOUTH | 1954 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR |  | SOUTH | 1954 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR |  | SOUTH | 1954 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
GRANITE SHOALS 1 |  | WIRTZ_WIRTZ_G1 | BURNET |  | SOUTH | 1951 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
GRANITE SHOALS 2 |  | WIRTZ_WIRTZ_G2 | BURNET |  | SOUTH | 1951 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
INKS 1 |  | INKSDA_INKS_G1 | LLANO |  | SOUTH | 1938 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
MARBLE FALLS 1 |  | MARBFA_MARBFAG1 | BURNET |  | SOUTH | 1951 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
MARBLE FALLS 2 |  | MARBFA_MARBFAG2 | BURNET |  | SOUTH | 1951 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
MARSHALL FORD 1 |  | MARSFO_MARSFOG1 | TRAVIS |  | SOUTH | 1941 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
MARSHALL FORD 2 |  | MARSFO_MARSFOG2 | TRAVIS |  | SOUTH | 1941 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
MARSHALL FORD 3 |  | MARSFO_MARSFOG3 | TRAVIS |  | SOUTH | 1941 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
WHITNEY DAM |  | WND_WHITNEY1 | BOSQUE |  | NORTH | 1953 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
WHITNEY 2 |  | WND_WHITNEY2 | BOSQUE |  | NORTH | 1953 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
Operational Capacity Total (Hydro) | [6 empty] | 540.7 | 540.7 | 540.7 | 540.7 | 540.7 | 540.7 | 540.7 | 540.7 | 540.7 | 540.7
Hydro Capacity Contribution (Average maximum capability for Top 20 Hours) |  |  |  | HYDRO |  |  | 446.2 | 446.2 | 446.2 | 446.2 | 446.2 | 446.2 | 446.2 | 446.2 | 446.2 | 446.2
Operational Capacity Total (Including Hydro) | [6 empty] | 63114.529 | 63114.529 | 63114.529 | 63114.529 | 63114.529 | 62274.529 | 62274.529 | 62274.529 | 62274.529 | 62274.529
Private Use Network (PUN) Capacity Contribution (Average maximum capability Top 20 Hours) |  |  |  | GAS |  |  | 4474 | 4474 | 4474 | 4474 | 4474 | 4474 | 4474 | 4474 | 4474 | 4474
NEW PUN UNITS | 14INR0016 |  | HARRIS | GAS | HOUSTON | 2014 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181
Capacity from Private Use Networks | [6 empty] | 4655 | 4655 | 4655 | 4655 | 4655 | 4655 | 4655 | 4655 | 4655 | 4655
RMR Capacity Total | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DC-Ties
EAGLE PASS |  | DC_S | MAVERICK |  | SOUTH |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
EAST |  | DC_E | FANNIN |  | NORTH |  | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
LAREDO VFT |  | DC_L | WEBB |  | SOUTH |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
NORTH |  | DC_N | WILBARGER |  | WEST |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
SHARYLAND (RAILROAD) |  | DC_R | HILDALGO |  | SOUTH |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SHARYLAND (NEW RAILROAD TIE) |  | DC_R2 | HILDALGO |  | SOUTH |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
DC-Tie Capacity Total | [6 empty] | 1256 | 1256 | 1256 | 1256 | 1256 | 1256 | 1256 | 1256 | 1256 | 1256
DC-Ties Capacity Contribution (Average maximum capability for Top 20 Hours) |  |  |  | OTHER |  |  | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3
Switchable Resources
KIAMICHI ENERGY FACILITY 1CT101 |  | KMCHI_1CT101 | PITTSBURG | GAS | NORTH | 2003 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
KIAMICHI ENERGY FACILITY 1CT201 |  | KMCHI_1CT201 | PITTSBURG | GAS | NORTH | 2003 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
KIAMICHI ENERGY FACILITY 1ST |  | KMCHI_1ST | PITTSBURG | GAS | NORTH | 2003 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315
KIAMICHI ENERGY FACILITY 2CT101 |  | KMCHI_2CT101 | PITTSBURG | GAS | NORTH | 2003 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
KIAMICHI ENERGY FACILITY 2CT201 |  | KMCHI_2CT201 | PITTSBURG | GAS | NORTH | 2003 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
KIAMICHI ENERGY FACILITY 2ST |  | KMCHI_2ST | PITTSBURG | GAS | NORTH | 2003 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315
TENASKA-FRONTIER 1 |  | FTR_FTR_G1 | GRIMES | GAS | HOUSTON | 2000 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
TENASKA-FRONTIER 2 |  | FTR_FTR_G2 | GRIMES | GAS | HOUSTON | 2000 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
TENASKA-FRONTIER 3 |  | FTR_FTR_G3 | GRIMES | GAS | HOUSTON | 2000 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
TENASKA-FRONTIER 4 |  | FTR_FTR_G4 | GRIMES | GAS | HOUSTON | 2000 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
TENASKA-GATEWAY 1 |  | TGCCS_CT1 | RUSK | GAS | NORTH | 2001 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156
TENASKA-GATEWAY 2 |  | TGCCS_CT2 | RUSK | GAS | NORTH | 2001 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135
TENASKA-GATEWAY 3 |  | TGCCS_CT3 | RUSK | GAS | NORTH | 2001 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
TENASKA-GATEWAY 4 |  | TGCCS_UNIT4 | RUSK | GAS | NORTH | 2001 | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 402
Switchable Capacity Total | [6 empty] | 2972 | 2972 | 2972 | 2972 | 2972 | 2972 | 2972 | 2972 | 2972 | 2972
Wind Resources
ANACACHO WINDFARM |  | ANACACHO_ANA | KINNEY | WIND | SOUTH | 2012 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101
BARTON CHAPEL WIND |  | BRTSW_BCW1 | JACK | WIND | WEST | 2007 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
BOBCAT WIND |  | BCATWIND_WIND_1 | ARCHER | WIND | NORTH | 2012 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
BLUE SUMMIT WIND 5 | 12INR0075 | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND | WEST | 2012 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
BLUE SUMMIT WIND 6 | 12INR0075 | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND | WEST | 2012 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4
BUFFALO GAP WIND FARM 1 |  | BUFF_GAP_UNIT1 | TAYLOR | WIND | WEST | 2006 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6
BUFFALO GAP WIND FARM 2 |  | BUFF_GAP_UNIT2_1 | TAYLOR | WIND | WEST | 2007 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5
BUFFALO GAP WIND FARM 2 |  | BUFF_GAP_UNIT2_2 | TAYLOR | WIND | WEST | 2007 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117
BUFFALO GAP WIND FARM 3 |  | BUFF_GAP_UNIT3 | TAYLOR | WIND | WEST | 2008 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2
BULL CREEK WIND PLANT |  | BULLCRK_WND1 | BORDEN | WIND | WEST | 2009 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88
BULL CREEK WIND PLANT |  | BULLCRK_WND2 | BORDEN | WIND | WEST | 2009 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
CALLAHAN WIND |  | CALLAHAN_WND1 | CALLAHAN | WIND | WEST | 2004 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114
CAMP SPRINGS 1 |  | CSEC_CSECG1 | SCURRY | WIND | WEST | 2007 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5
CAMP SPRINGS 2 |  | CSEC_CSECG2 | SCURRY | WIND | WEST | 2007 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
CAPRICORN RIDGE WIND 1 |  | CAPRIDGE_CR1 | STERLING | WIND | WEST | 2007 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5
CAPRICORN RIDGE WIND 2 |  | CAPRIDGE_CR3 | STERLING | WIND | WEST | 2008 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186
CAPRICORN RIDGE WIND 3 |  | CAPRIDGE_CR2 | STERLING | WIND | WEST | 2007 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5
CAPRICORN RIDGE WIND 4 |  | CAPRIDG4_CR4 | COKE/STERLING | WIND | WEST | 2008 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5
CEDRO HILL WIND |  | CEDROHIL_CHW1 | WEBB | WIND | SOUTH | 2010 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
CHAMPION WIND FARM |  | CHAMPION_UNIT1 | NOLAN/MITCHELL | WIND | WEST | 2008 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5
DELAWARE MOUNTAIN WIND FARM |  | KUNITZ_WIND_NWP | CULBERSON | WIND | WEST | 1999 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5
DESERT SKY WIND FARM 1 |  | INDNENR_INDNENR | PECOS | WIND | WEST | 2002 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
DESERT SKY WIND FARM 2 |  | INDNENR_INDNENR_2 | PECOS | WIND | WEST | 2002 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5
ELBOW CREEK WIND PROJECT |  | ELB_ELBCREEK | HOWARD | WIND | WEST | 2008 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7
FOREST CREEK WIND FARM |  | MCDLD_FCW1 | GLASSCOCK | WIND | WEST | 2007 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2
GOAT WIND |  | GOAT_GOATWIND | STERLING | WIND | WEST | 2008 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
GOAT WIND 2 |  | GOAT_GOATWIN2 | STERLING | WIND | WEST | 2010 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6
GREEN MOUNTAIN ENERGY 1 |  | BRAZ_WND_WND1 | SCURRY/BORDEN | WIND | WEST | 2003 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99
GREEN MOUNTAIN ENERGY 2 |  | BRAZ_WND_WND2 | SCURRY/BORDEN | WIND | WEST | 2003 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
GULF WIND I |  | TGW_T1 | KENEDY | WIND | SOUTH | 2010 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
GULF WIND II |  | TGW_T2 | KENEDY | WIND | SOUTH | 2010 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
HACKBERRY WIND FARM |  | HWF_HWFG1 | SHACKELFORD | WIND | WEST | 2008 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5
HARBOR WIND |  | DG_NUECE_6UNITS | NUECES | WIND | SOUTH | 2012 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
HORSE HOLLOW WIND 1 |  | H_HOLLOW_WND1 | TAYLOR | WIND | WEST | 2005 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213
HORSE HOLLOW WIND 2 |  | HHOLLOW2_WIND1 | TAYLOR | WIND | WEST | 2006 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184
HORSE HOLLOW WIND 3 |  | HHOLLOW3_WND_1 | TAYLOR | WIND | WEST | 2006 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5
HORSE HOLLOW WIND 4 |  | HHOLLOW4_WND1 | TAYLOR | WIND | WEST | 2006 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115
INADALE WIND |  | INDL_INADALE1 | NOLAN | WIND | WEST | 2008 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6
INDIAN MESA WIND FARM |  | INDNNWP_INDNNWP | PECOS | WIND | WEST | 2001 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5
KING MOUNTAIN NE |  | KING_NE_KINGNE | UPTON | WIND | WEST | 2001 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3
KING MOUNTAIN NW |  | KING_NW_KINGNW | UPTON | WIND | WEST | 2001 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3
KING MOUNTAIN SE |  | KING_SE_KINGSE | UPTON | WIND | WEST | 2001 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3
KING MOUNTAIN SW |  | KING_SW_KINGSW | UPTON | WIND | WEST | 2001 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3
KUNITZ WIND |  | KUNITZ_WIND_LGE | CULBERSON | WIND | WEST | 1995 | 39.8 | 39.8 | 39.8 | 39.8 | 39.8 | 39.8 | 39.8 | 39.8 | 39.8 | 39.8
LANGFORD WIND POWER |  | LGD_LANGFORD | TOM GREEN | WIND | WEST | 2009 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
LORAINE WINDPARK I |  | LONEWOLF_G1 | MITCHELL | WIND | WEST | 2009 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5
LORAINE WINDPARK II |  | LONEWOLF_G2 | MITCHELL | WIND | WEST | 2009 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51
LORAINE WINDPARK III |  | LONEWOLF_G3 | MITCHELL | WIND | WEST | 2011 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5
LORAINE WINDPARK IV |  | LONEWOLF_G4 | MITCHELL | WIND | WEST | 2011 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
LOS VIENTOS WIND I |  | LV1_LV1A | WILLACY | WIND | SOUTH | 2013 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1
LOS VIENTOS WIND II |  | LV1_LV1B | WILLACY | WIND | SOUTH | 2013 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6
MAGIC VALLEY WIND |  | REDFISH_MV1A | WILLACY | WIND | SOUTH | 2012 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103
MAGIC VALLEY WIND |  | REDFISH_MV1B | WILLACY | WIND | SOUTH | 2012 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103
MCADOO WIND FARM |  | MWEC_G1 | DICKENS | WIND | WEST | 2008 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
MESQUITE WIND |  | LNCRK_G83 | SHACKELFORD | WIND | WEST | 2006 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
NOTREES WIND 1 |  | NWF_NWF1 | WINKLER/ECTOR | WIND | WEST | 2009 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6
NOTREES WIND 2 |  | NWF_NWF2 | WINKLER/ECTOR | WIND | WEST | 2009 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OCOTILLO WIND FARM |  | OWF_OWF | HOWARD | WIND | WEST | 2008 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8
PANTHER CREEK 1 |  | PC_NORTH_PANTHER1 | HOWARD | WIND | WEST | 2008 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5
PANTHER CREEK 2 |  | PC_SOUTH_PANTHER2 | HOWARD | WIND | WEST | 2008 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5
PANTHER CREEK 3 |  | PC_SOUTH_PANTHER3 | HOWARD | WIND | WEST | 2009 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5
PAPALOTE CREEK WIND |  | COTTON_PAP2 | SAN PATRICIO | WIND | SOUTH | 2010 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1
PAPALOTE CREEK WIND FARM |  | PAP1_PAP1 | SAN PATRICIO | WIND | SOUTH | 2009 | 179.85 | 179.85 | 179.85 | 179.85 | 179.85 | 179.85 | 179.85 | 179.85 | 179.85 | 179.85
PECOS WIND (WOODWARD 1) |  | WOODWRD1_WOODWRD1 | PECOS | WIND | WEST | 2001 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5
PECOS WIND (WOODWARD 2) |  | WOODWRD2_WOODWRD2 | PECOS | WIND | WEST | 2001 | 77.22 | 77.22 | 77.22 | 77.22 | 77.22 | 77.22 | 77.22 | 77.22 | 77.22 | 77.22
PENASCAL WIND |  | PENA_UNIT1 | KENEDY | WIND | SOUTH | 2009 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8
PENASCAL WIND |  | PENA_UNIT2 | KENEDY | WIND | SOUTH | 2009 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
PENASCAL WIND |  | PENA3_UNIT3 | KENEDY | WIND | SOUTH | 2011 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8
POST OAK WIND 1 |  | LNCRK2_G871 | SHACKELFORD | WIND | WEST | 2007 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
POST OAK WIND 2 |  | LNCRK2_G872 | SHACKELFORD | WIND | WEST | 2007 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
PYRON WIND FARM |  | PYR_PYRON1 | SCURRY/FISHER | WIND | WEST | 2008 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249
RED CANYON |  | RDCANYON_RDCNY1 | BORDEN | WIND | WEST | 2006 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
ROSCOE WIND FARM |  | TKWSW1_ROSCOE | NOLAN | WIND | WEST | 2008 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209
SAND BLUFF WIND FARM |  | MCDLD_SBW1 | GLASSCOCK | WIND | WEST | 2008 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
SENATE WIND PROJECT |  | SENATEWD_UNIT1 | JACK | WIND | WEST | 2012 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SHERBINO I |  | KEO_KEO_SM1 | PECOS | WIND | WEST | 2008 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SHERBINO 2 |  | KEO_SHRBINO2 | PECOS | WIND | WEST | 2011 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SILVER STAR |  | FLTCK_SSI | EASTLAND | WIND | NORTH | 2008 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SNYDER WIND FARM |  | ENAS_ENA1 | SCURRY | WIND | WEST | 2007 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
SOUTH TRENT WIND FARM |  | STWF_T1 | NOLAN/TAYLOR | WIND | WEST | 2008 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2
STANTON WIND ENERGY |  | SWEC_G1 | MARTIN | WIND | WEST | 2008 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
SWEETWATER WIND 1 |  | SWEETWND_WND1 | NOLAN | WIND | WEST | 2003 | 36.58 | 36.58 | 36.58 | 36.58 | 36.58 | 36.58 | 36.58 | 36.58 | 36.58 | 36.58
SWEETWATER WIND 2 |  | SWEETWN2_WND24 | NOLAN | WIND | WEST | 2006 | 15.87 | 15.87 | 15.87 | 15.87 | 15.87 | 15.87 | 15.87 | 15.87 | 15.87 | 15.87
SWEETWATER WIND 3 |  | SWEETWN2_WND2 | NOLAN | WIND | WEST | 2004 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5
SWEETWATER WIND 4 |  | SWEETWN3_WND3A | NOLAN | WIND | WEST | 2011 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5
SWEETWATER WIND 4 |  | SWEETWN3_WND3B | NOLAN | WIND | WEST | 2011 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5
SWEETWATER WIND 5 |  | SWEETWN4_WND5 | NOLAN | WIND | WEST | 2007 | 79.23 | 79.23 | 79.23 | 79.23 | 79.23 | 79.23 | 79.23 | 79.23 | 79.23 | 79.23
SWEETWATER WIND 6 |  | SWEETWN4_WND4B | NOLAN | WIND | WEST | 2007 | 103.65 | 103.65 | 103.65 | 103.65 | 103.65 | 103.65 | 103.65 | 103.65 | 103.65 | 103.65
SWEETWATER WIND 7 |  | SWEETWN4_WND4A | NOLAN | WIND | WEST | 2007 | 117.8 | 117.8 | 117.8 | 117.8 | 117.8 | 117.8 | 117.8 | 117.8 | 117.8 | 117.8
TEXAS BIG SPRING |  | SGMTN_SIGNALMT | HOWARD | WIND | WEST | 1999 | 34.32 | 34.32 | 34.32 | 34.32 | 34.32 | 34.32 | 34.32 | 34.32 | 34.32 | 34.32
TRENT WIND FARM |  | TRENT_TRENT | NOLAN | WIND | WEST | 2001 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
TRINITY HILLS |  | TRINITY_TH1_BUS1 | YOUNG | WIND | NORTH | 2012 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5
TRINITY HILLS |  | TRINITY_TH1_BUS2 | YOUNG | WIND | NORTH | 2012 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5
TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | NOLAN | WIND | WEST | 2008 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
TURKEY TRACK WIND ENERGY CENTER |  | TTWEC_G1 | NOLAN | WIND | WEST | 2008 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5
WEST TEXAS WIND ENERGY |  | SW_MESA_SW_MESA | UPTON/CROCKETT | WIND | WEST | 1999 | 74.2 | 74.2 | 74.2 | 74.2 | 74.2 | 74.2 | 74.2 | 74.2 | 74.2 | 74.2
WHIRLWIND ENERGY |  | WEC_WECG1 | FLOYD | WIND | NORTH | 2007 | 56.957 | 56.957 | 56.957 | 56.957 | 56.957 | 56.957 | 56.957 | 56.957 | 56.957 | 56.957
WHITETAIL WIND ENERGY PROJECT |  | EXGNWTL_WIND_1 | WEBB/DUVAL | WIND | SOUTH | 2012 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
WKN MOZART |  | MOZART_WIND_1 | KENT/STONEWALL | WIND | WEST | 2012 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
WOLFE RIDGE |  | WHTTAIL_WR1 | COOKE | WIND | NORTH | 2008 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5
Wind Capacity Total | [6 empty] | 11065.777 | 11065.777 | 11065.777 | 11065.777 | 11065.777 | 11065.777 | 11065.777 | 11065.777 | 11065.777 | 11065.777
Wind Capacity Total (Non-Coastal) | [6 empty] | 9382.727 | 9382.727 | 9382.727 | 9382.727 | 9382.727 | 9382.727 | 9382.727 | 9382.727 | 9382.727 | 9382.727
Wind Capacity Total (Coastal) | [6 empty] | 1683.05 | 1683.05 | 1683.05 | 1683.05 | 1683.05 | 1683.05 | 1683.05 | 1683.05 | 1683.05 | 1683.05
Wind Capacity (Coastal County) |  |  | SAN PATRICIO |  | SOUTH |  | 379.95 | 379.95 | 379.95 | 379.95 | 379.95 | 379.95 | 379.95 | 379.95 | 379.95 | 379.95
Wind Capacity (Coastal County) |  |  | NUECES |  | SOUTH |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
Wind Capacity (Coastal County) |  |  | KLEBERG |  | SOUTH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind Capacity (Coastal County) |  |  | KENEDY |  | SOUTH |  | 686.4 | 686.4 | 686.4 | 686.4 | 686.4 | 686.4 | 686.4 | 686.4 | 686.4 | 686.4
Wind Capacity (Coastal County) |  |  | WILLACY |  | SOUTH |  | 607.7 | 607.7 | 607.7 | 607.7 | 607.7 | 607.7 | 607.7 | 607.7 | 607.7 | 607.7
Wind Capacity (Coastal County) |  |  | CAMERON |  | SOUTH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
New Resources with Signed IA and Air Permit
PANDA SHERMAN CTG1 | 10INR0021 | PANDA_S_SHER1CT1 | GRAYSON | GAS | NORTH | 2014 | 0 | 192.75 | 192.75 | 192.75 | 192.75 | 192.75 | 192.75 | 192.75 | 192.75 | 192.75
PANDA SHERMAN CTG2 | 10INR0021 | PANDA_S_SHER1CT2 | GRAYSON | GAS | NORTH | 2014 | 0 | 192.75 | 192.75 | 192.75 | 192.75 | 192.75 | 192.75 | 192.75 | 192.75 | 192.75
PANDA SHERMAN STG | 10INR0021 | PANDA_S_SHER1ST1 | GRAYSON | GAS | NORTH | 2014 | 0 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7
PANDA TEMPLE CTG1 | 10INR0020a | PANDA_T1_TMPL1CT1 | BELL | GAS | NORTH | 2014 | 0 | 191.15 | 191.15 | 191.15 | 191.15 | 191.15 | 191.15 | 191.15 | 191.15 | 191.15
PANDA TEMPLE CTG2 | 10INR0020a | PANDA_T1_TMPL1CT2 | BELL | GAS | NORTH | 2014 | 0 | 191.15 | 191.15 | 191.15 | 191.15 | 191.15 | 191.15 | 191.15 | 191.15 | 191.15
PANDA TEMPLE STG | 10INR0020a | PANDA_T1_TMPL1ST1 | BELL | GAS | NORTH | 2014 | 0 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7
DEER PARK ENERGY CENTER | 14INR0015 | DDPEC_GT6 | HARRIS | GAS | HOUSTON | 2014 | 0 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
FERGUSON REPLACEMENT CTG1 | 13INR0021 | FERGCC_FERGGT1 | LLANO | GAS | SOUTH | 2014 | 0 | 161.9 | 161.9 | 161.9 | 161.9 | 161.9 | 161.9 | 161.9 | 161.9 | 161.9
FERGUSON REPLACEMENT CTG2 | 13INR0021 | FERGCC_FERGGT2 | LLANO | GAS | SOUTH | 2014 | 0 | 161.9 | 161.9 | 161.9 | 161.9 | 161.9 | 161.9 | 161.9 | 161.9 | 161.9
FERGUSON REPLACEMENT STG | 13INR0021 | FERGCC_FERGST1 | LLANO | GAS | SOUTH | 2014 | 0 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186
TEXAS CLEAN ENERGY PROJECT | 13INR0023 |  | ECTOR | COAL | WEST | 2018 | 0 | 0 | 0 | 0 | 0 | 240 | 240 | 240 | 240 | 240
PANDA TEMPLE II | 10INR0020b |  | BELL | GAS | NORTH | 2015 | 0 | 0 | 717 | 717 | 717 | 717 | 717 | 717 | 717 | 717
PONDERA KING POWER PROJECT | 10INR0022 |  | HARRIS | GAS | HOUSTON | 2018 | 0 | 0 | 0 | 0 | 1468.6 | 1468.6 | 1468.6 | 1468.6 | 1468.6 | 1468.6
RENTECH PROJECT | 13INR0040 |  | HARRIS | GAS | HOUSTON | 2014 | 0 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
FORNEY POWER UPGRADE GT11-13 | 14INR0059 |  | KAUFMAN | GAS | NORTH | 2014 | 0 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
FORNEY POWER UPGRADE GT21-23 | 14INR0059 |  | KAUFMAN | GAS | NORTH | 2015 | 0 | 0 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
WHITE CAMP SOLAR | 11INR0094 | WCSOLAR1_100PV | KENT | SOLAR | WEST | 2014 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
MUSTANG SOLAR PROJECT | 13INR0031 |  | TRAVIS | SOLAR | SOUTH | 2015 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
OCI ALAMO 4 | 14INR0024 |  | KINNEY | SOLAR | SOUTH | 2014 | 0 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6
PECOS BARILLA SOLAR | 12INR0059 | HOVEY_UNIT1 | PECOS | SOLAR | WEST | 2014 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
New Capacity Total (Not Wind) | [6 empty] | 130 | 2320.6 | 3093.6 | 3093.6 | 4562.2 | 4802.2 | 4802.2 | 4802.2 | 4802.2 | 4802.2
New Wind Resources
STEPHENS RANCH WIND ENERGY | 12INR0034 |  | BORDEN | WIND | WEST | 2014 | 0 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378
GOLDTHWAITE WIND 1 | 11INR0013 | GWEC_GWEC_G1 | MILLS | WIND | NORTH | 2014 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6
SPINNING SPUR WIND TWO | 13INR0048 | SSPURTWO_WIND_1 | OLDHAM | WIND | PANHANDLE | 2014 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161
MARIAH WIND a | 13INR0010a |  | PARMER | WIND | PANHANDLE | 2014 | 0 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232
PANHANDLE WIND | 14INR0030a_2 |  | CARSON | WIND | PANHANDLE | 2014 | 0 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218
PANHANDLE WIND 2 | 14INR0030b |  | CARSON | WIND | PANHANDLE | 2015 | 0 | 0 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182
MIAMI WIND 1a | 14INR0012a | MIAM1_G1, G2 | GRAY | WIND | PANHANDLE | 2014 | 0 | 288.9 | 288.9 | 288.9 | 288.9 | 288.9 | 288.9 | 288.9 | 288.9 | 288.9
MOORE WIND 1 | 11INR0050 |  | CROSBY | WIND | WEST | 2014 | 0 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149
MARIAH WIND | 13INR0010b |  | PARMER | WIND | PANHANDLE | 2015 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
MIDWAY FARMS WIND | 11INR0054 |  | SAN PATRICIO | WIND | SOUTH | 2015 | 0 | 0 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161
LONGHORN ENERGY CENTER | 14INR0023 |  | BRISCOE | WIND | WEST | 2014 | 0 | 361 | 361 | 361 | 361 | 361 | 361 | 361 | 361 | 361
CONWAY WINDFARM | 13INR0005 |  | CARSON | WIND | PANHANDLE | 2014 | 0 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
SOUTH CLAY WINDFARM | 11INR0079a |  | CLAY | WIND | WEST | 2014 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
PENASCAL WIND FARM 3 | 06INR0022c |  | KENEDY | WIND | SOUTH | 2014 | 0 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202
MARIAH WIND c | 13INR0010c |  | PARMER | WIND | PANHANDLE | 2016 | 0 | 0 | 0 | 168 | 168 | 168 | 168 | 168 | 168 | 168
MESQUITE CREEK | 09INR0051 |  | BORDEN | WIND | WEST | 2015 | 0 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249
GUNSIGHT MOUNTAIN | 08INR0018 |  | HOWARD | WIND | WEST | 2015 | 0 | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
BRISCOE WIND FARM | 14INR0072 |  | BRISCOE | WIND | WEST | 2015 | 0 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
CAMERON COUNTY WIND | 11INR0057 |  | CAMERON | WIND | SOUTH | 2015 | 0 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
COMANCHE RUN WIND | 12INR0029 |  | SWISHER | WIND | PANHANDLE | 2016 | 0 | 0 | 0 | 500 | 500 | 500 | 500 | 500 | 500 | 500
CPV RATTLESNAKE DEN PH 1 | 13INR0020a |  | GLASSCOCK | WIND | WEST | 2015 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
CPV RATTLESNAKE DEN PH 2 | 13INR0020b |  | GLASSCOCK | WIND | WEST | 2016 | 0 | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
GREEN PASTURES WIND | 12INR0070 |  | KNOX | WIND | WEST | 2015 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
HEREFORD WIND a | 13INR0059a |  | CASTRO | WIND | PANHANDLE | 2014 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
JUMBO ROAD WIND b | 13INR0059b |  | CASTRO | WIND | PANHANDLE | 2015 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
KEECHI WIND 138 KV JOPLIN | 14INR0049_2 |  | JACK | WIND | NORTH | 2014 | 0 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
LOGANS GAP WIND I | 13INR0050 |  | COMANCHE | WIND | NORTH | 2015 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
LOS VIENTOS III | 13INR0052 |  | STARR | WIND | SOUTH | 2014 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
MIAMI WIND 1b | 14INR0012b |  | GRAY | WIND | PANHANDLE | 2015 | 0 | 0 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111
PAMPA WIND PROJECT | 12INR0018 |  | GRAY | WIND | PANHANDLE | 2017 | 0 | 0 | 0 | 500 | 500 | 500 | 500 | 500 | 500 | 500
PATRIOT (PETRONILLA) WIND | 11INR0062 |  | NUECES | WIND | SOUTH | 2015 | 0 | 0 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
ROUTE66 WIND | 14INR0032a |  | RANDALL | WIND | PANHANDLE | 2014 | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SENDERO WIND ENERGY PROJECT | 12INR0068 |  | JIM HOGG | WIND | SOUTH | 2015 | 0 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
SOUTH PLAINS WIND I | 14INR0025a |  | FLOYD | WIND | WEST | 2015 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
SOUTH PLAINS WIND II | 14INR0025b |  | FLOYD | WIND | WEST | 2015 | 0 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
SPINNING SPUR WIND THREE | 14INR0053 |  | OLDHAM | WIND | PANHANDLE | 2014 | 0 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194
WINDTHORST 2 | 13INR0057 |  | ARCHER | WIND | NORTH | 2014 | 0 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
New Wind Capacity Total | [6 empty] | 309.6 | 5341.5 | 7243.5 | 8411.5 | 8411.5 | 8411.5 | 8411.5 | 8411.5 | 8411.5 | 8411.5
New Wind Capacity Total (Non-Coastal) | [6 empty] | 309.6 | 4974.5 | 6537.5 | 7705.5 | 7705.5 | 7705.5 | 7705.5 | 7705.5 | 7705.5 | 7705.5
New Wind Capacity Total (Coastal) | [6 empty] | 0 | 367 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706
New Wind Capacity (Coastal County) |  |  | SAN PATRICIO |  | SOUTH |  | 0 | 0 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161
New Wind Capacity (Coastal County) |  |  | NUECES |  | SOUTH |  | 0 | 0 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
New Wind Capacity (Coastal County) |  |  | KLEBERG |  | SOUTH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
New Wind Capacity (Coastal County) |  |  | KENEDY |  | SOUTH |  | 0 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202
New Wind Capacity (Coastal County) |  |  | WILLACY |  | SOUTH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
New Wind Capacity (Coastal County) |  |  | CAMERON |  | SOUTH |  | 0 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
Switchable Capacity Unavailable to ERCOT |  |  |  | GAS |  |  | -300 | -300 | -300 | -300 | -300 | -300 | -300 | 0 | 0 | 0
Available Mothball Capacity based on Owner's Return Probability |  |  |  | COAL |  |  | 2602 | 2660 | 1933 | 1933 | 1933 | 1933 | 1933 | 1933 | 1933 | 1933
Retiring Capacity
AES DEEPWATER |  | APD_APD_PS1 | HARRIS | STORAGE | HOUSTON | 2010 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
Total Retiring Units | [6 empty] | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
Mothballed Capacity
APPLIED ENERGY |  | APD_APD_G1 | HARRIS | OTHER | HOUSTON | 1986 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138
ATKINS |  | ATKINS_ATKINSG3 | BRAZOS | GAS | NORTH | 1954 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
ATKINS |  | ATKINS_ATKINSG4 | BRAZOS | GAS | NORTH | 1958 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
ATKINS |  | ATKINS_ATKINSG5 | BRAZOS | GAS | NORTH | 1965 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
ATKINS |  | ATKINS_ATKINSG6 | BRAZOS | GAS | NORTH | 1969 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
GREENS BAYOU |  | GBY_GBYGT82 | HARRIS | GAS | HOUSTON | 1976 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58
NORTH TEXAS |  | NTX_NTX_1 | PARKER | GAS | NORTH | 1958 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
NORTH TEXAS |  | NTX_NTX_2 | PARKER | GAS | NORTH | 1958 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
NORTH TEXAS |  | NTX_NTX_3 | PARKER | GAS | NORTH | 1963 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
PERMIAN BASIN SES |  | PBSES_UNIT6 | WARD | GAS | WEST | 1973 | 515 | 515 | 515 | 515 | 515 | 515 | 515 | 515 | 515 | 515
SILAS RAY |  | SILASRAY_SILAS_5 | CAMERON | GAS | SOUTH | 1953 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
VALLEY SES |  | VLSES_UNIT1 | FANNIN | GAS | NORTH | 1962 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174
VALLEY SES |  | VLSES_UNIT2 | FANNIN | GAS | NORTH | 1967 | 520 | 520 | 520 | 520 | 520 | 520 | 520 | 520 | 520 | 520
VALLEY SES |  | VLSES_UNIT3 | FANNIN | GAS | NORTH | 1971 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375
J T DEELY 1 |  | CALAVERS_JTD1 | BEXAR | COAL | SOUTH | 1977 | 0 | 0 | 0 | 0 | 0 | 420 | 420 | 420 | 420 | 420
J T DEELY 2 |  | CALAVERS_JTD2 | BEXAR | COAL | SOUTH | 1978 | 0 | 0 | 0 | 0 | 0 | 420 | 420 | 420 | 420 | 420
SR BERTRON |  | SRB_SRBGT_2 | HARRIS | GAS | HOUSTON | 1967 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
SR BERTRON |  | SRB_SRB_G1 | HARRIS | GAS | HOUSTON | 1958 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118
SR BERTRON |  | SRB_SRB_G2 | HARRIS | GAS | HOUSTON | 1956 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174
SR BERTRON |  | SRB_SRB_G3 | HARRIS | GAS | HOUSTON | 1959 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211
SR BERTRON |  | SRB_SRB_G4 | HARRIS | GAS | HOUSTON | 1960 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211
Total Mothballed Capacity | [6 empty] | 2701 | 2701 | 2701 | 2701 | 2701 | 3541 | 3541 | 3541 | 3541 | 3541
Seasonal Mothballed Capacity
MARTIN LAKE 3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 805 | 805 | 805 | 805 | 805 | 805 | 805 | 805 | 805 | 805
MONTICELLO 1 |  | MNSES_UNIT1 | TITUS | COAL | NORTH | 1974 | 535 | 535 | 535 | 535 | 535 | 535 | 535 | 535 | 535 | 535
MONTICELLO 2 |  | MNSES_UNIT2 | TITUS | COAL | NORTH | 1975 | 535 | 535 | 535 | 535 | 535 | 535 | 535 | 535 | 535 | 535
Total Seasonal Mothballed Capacity | [6 empty] | 1875 | 1875 | 1875 | 1875 | 1875 | 1875 | 1875 | 1875 | 1875 | 1875
Excluded Resources, per notification from developer
COBISA-GREENVILLE | 06INR0006 |  | HUNT | GAS |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Note on M622: Adjusted based on Notice of Suspension of Operations (NOS) dated 10/25/2013.

## WinterSummary
2014 Report on the Capacity, Demand, and Reserves in the ERCOT Region
Winter Summary
| Load Forecast: |  | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24
|  | Total Winter Peak Demand, MW | 52837.006 | 53719.121 | 54579.312 | 55440.7278 | 56280.6432 | 57115.7777 | 57962.0193 | 58804.466 | 59642.616 | 60479.6487
|  | less LRS Serving as Responsive Reserve, MW | 1230.6203 | 1230.6203 | 1230.6203 | 1230.6203 | 1230.6203 | 1230.6203 | 1230.6203 | 1230.6203 | 1230.6203 | 1230.6203
|  | less LRS Serving as Non-Spinning Reserve, MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | less Emergency Response Service (10- and 30-min ramp products) | 844.462 | 1055.8139 | 1055.8139 | 1055.8139 | 1055.8139 | 1055.8139 | 1055.8139 | 1055.8139 | 1055.8139 | 1055.8139
|  | less TDSP Standard Offer Load Management Programs | 254.8243 | 254.8243 | 254.8243 | 254.8243 | 254.8243 | 254.8243 | 254.8243 | 254.8243 | 254.8243 | 254.8243
|  | Firm Load Forecast, MW | 50507.0994 | 51177.8624 | 52038.0534 | 52899.4692 | 53739.3847 | 54574.5192 | 55420.7607 | 56263.2074 | 57101.3574 | 57938.3901
| Resources: |  | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24
|  | Installed Capacity, MW | 65298.2991 | 65298.2991 | 65298.2991 | 65298.2991 | 65298.2991 | 64448.2991 | 64448.2991 | 64448.2991 | 64448.2991 | 64448.2991
|  | Capacity from Private Networks, MW | 4668 | 4668 | 4668 | 4668 | 4668 | 4668 | 4668 | 4668 | 4668 | 4668
|  | Effective Load-Carrying Capability (ELCC) of Non-Coastal Wind (8.7%), MW | 816.2972 | 816.2972 | 816.2972 | 816.2972 | 816.2972 | 816.2972 | 816.2972 | 816.2972 | 816.2972 | 816.2972
|  | Effective Load-Carrying Capability (ELCC) of Coastal Wind (8.7%), MW | 146.4253 | 146.4253 | 146.4253 | 146.4253 | 146.4253 | 146.4253 | 146.4253 | 146.4253 | 146.4253 | 146.4253
|  | RMR Capacity to be under Contract, MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Operational Generation, MW | 70929.0217 | 70929.0217 | 70929.0217 | 70929.0217 | 70929.0217 | 70079.0217 | 70079.0217 | 70079.0217 | 70079.0217 | 70079.0217
|  | Capacity Contribution of Non-Synchronous Ties (top 20 hrs), MW | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3
|  | Switchable Capacity, MW | 3178 | 3178 | 3178 | 3178 | 3178 | 3178 | 3178 | 3178 | 3178 | 3178
|  | Available Mothballed Capacity, MW | 0 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58
|  | Planned Resources (not wind) with Signed IA and Air Permit, MW | 2501.4 | 3308.4 | 3338.4 | 3338.4 | 5207.37 | 5207.37 | 5207.37 | 5207.37 | 5207.37 | 5207.37
|  | ELCC of Planned Non-Coastal Wind with Signed IA (8.7%), MW | 251.1255 | 512.2995 | 568.8495 | 670.4655 | 670.4655 | 670.4655 | 670.4655 | 670.4655 | 670.4655 | 670.4655
|  | ELCC of Planned Coastal Wind with Signed IA (8.7%), MW | 0 | 61.422 | 61.422 | 61.422 | 61.422 | 61.422 | 61.422 | 61.422 | 61.422 | 61.422
|  | Total Resources, MW | 77502.8472 | 78690.4432 | 78776.9932 | 78878.6092 | 80747.5791 | 79897.5791 | 79897.5791 | 79897.5791 | 79897.5791 | 79897.5791
|  | less Switchable Capacity Unavailable to ERCOT, MW | -330 | -330 | -330 | -330 | -330 | -330 | -330 | 0 | 0 | 0
less Retiring Capacity, MW | bar: 2014/15 to 2023/24
|  | Resources, MW | 77171.8472 | 78359.4432 | 78445.9932 | 78547.6092 | 80416.5791 | 79566.5791 | 79566.5791 | 79896.5791 | 79896.5791 | 79896.5791
|  | Reserve Margin | 52.79% | 53.11% | 50.75% | 48.48% | 49.64% | 45.79% | 43.57% | 42.01% | 39.92% | 37.9%
(Resources - Firm Load Forecast)/Firm Load Forecast
2014 Report on the Capacity, Demand, and Reserves in the ERCOT Region
Winter Loads and Resources
|  |  | 57451.8255 | 58214.8185 | 59193.2858 | 60173.1462 | 61128.55 | 62078.5156 | 63041.1153 | 63999.3984 | 64952.7941 | 65904.9187

## WinterCapacities
Unit Capacities - Winter
Units used in determining the generation resources in the Summer Summary
Operational capacities are based on unit testing. Other capacities are based on information provided by the plant owners. This list includes MW available to the grid from private network (self-serve) units. It also includes distributed generation units that have registered with ERCOT. Data without unit names are for private network units or are planned generation that is not public.
[7 empty] | Winter | Winter | Winter | Winter | Winter | Winter | Winter | Winter | Winter | Winter
SITE_NAME | GINR_NUM | UNIT_CODE | COUNTY | FUEL | ZONE | YEAR | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023
BIG BROWN 1 |  | BBSES_UNIT1 | FREESTONE | COAL | NORTH | 1971 | 606 | 606 | 606 | 606 | 606 | 606 | 606 | 606 | 606 | 606
BIG BROWN 2 |  | BBSES_UNIT2 | FREESTONE | COAL | NORTH | 1972 | 602 | 602 | 602 | 602 | 602 | 602 | 602 | 602 | 602 | 602
COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650
FAYETTE POWER PROJECT 1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 603 | 603 | 603 | 603 | 603 | 603 | 603 | 603 | 603 | 603
FAYETTE POWER PROJECT 2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 605 | 605 | 605 | 605 | 605 | 605 | 605 | 605 | 605 | 605
FAYETTE POWER PROJECT 3 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449
GIBBONS CREEK 1 |  | GIBCRK_GIB_CRG1 | GRIMES | COAL | NORTH | 1983 | 470 | 470 | 470 | 470 | 470 | 470 | 470 | 470 | 470 | 470
J K SPRUCE 1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 562 | 562 | 562 | 562 | 562 | 562 | 562 | 562 | 562 | 562
J K SPRUCE 2 |  | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 775 | 775 | 775 | 775 | 775 | 775 | 775 | 775 | 775 | 775
J T DEELY 1 |  | CALAVERS_JTD1 | BEXAR | COAL | SOUTH | 1977 | 430 | 430 | 430 | 430 | 430 | 0 | 0 | 0 | 0 | 0
J T DEELY 2 |  | CALAVERS_JTD2 | BEXAR | COAL | SOUTH | 1978 | 420 | 420 | 420 | 420 | 420 | 0 | 0 | 0 | 0 | 0
LIMESTONE 1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 831 | 831 | 831 | 831 | 831 | 831 | 831 | 831 | 831 | 831
LIMESTONE 2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 858 | 858 | 858 | 858 | 858 | 858 | 858 | 858 | 858 | 858
MARTIN LAKE 1 |  | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 815 | 815 | 815 | 815 | 815 | 815 | 815 | 815 | 815 | 815
MARTIN LAKE 2 |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820
MONTICELLO 3 |  | MNSES_UNIT3 | TITUS | COAL | NORTH | 1978 | 795 | 795 | 795 | 795 | 795 | 795 | 795 | 795 | 795 | 795
OAK GROVE SES UNIT 1 |  | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 840 | 840 | 840 | 840 | 840 | 840 | 840 | 840 | 840 | 840
OAK GROVE SES UNIT 2 |  | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 825 | 825 | 825 | 825 | 825 | 825 | 825 | 825 | 825 | 825
OKLAUNION 1 |  | OKLA_OKLA_G1 | WILBARGER | COAL | WEST | 1986 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650
SAN MIGUEL 1 |  | SANMIGL_SANMIGG1 | ATASCOSA | COAL | SOUTH | 1982 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391
SANDOW 5 |  | SD5SES_UNIT5 | MILAM | COAL | SOUTH | 2010 | 570 | 570 | 570 | 570 | 570 | 570 | 570 | 570 | 570 | 570
TWIN OAKS 1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158
TWIN OAKS 2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158
W A PARISH 5 |  | WAP_WAP_G5 | FORT BEND | COAL | HOUSTON | 1977 | 659 | 659 | 659 | 659 | 659 | 659 | 659 | 659 | 659 | 659
W A PARISH 6 |  | WAP_WAP_G6 | FORT BEND | COAL | HOUSTON | 1978 | 658 | 658 | 658 | 658 | 658 | 658 | 658 | 658 | 658 | 658
W A PARISH 7 |  | WAP_WAP_G7 | FORT BEND | COAL | HOUSTON | 1980 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577
W A PARISH 8 |  | WAP_WAP_G8 | FORT BEND | COAL | HOUSTON | 1982 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610
SANDY CREEK 1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 970 | 970 | 970 | 970 | 970 | 970 | 970 | 970 | 970 | 970
A VON ROSENBERG 1-CT1 |  | BRAUNIG_AVR1_CT1 | BEXAR | GAS | SOUTH | 2000 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
A VON ROSENBERG 1-CT2 |  | BRAUNIG_AVR1_CT2 | BEXAR | GAS | SOUTH | 2000 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
A VON ROSENBERG 1-ST1 |  | BRAUNIG_AVR1_ST | BEXAR | GAS | SOUTH | 2000 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184
ATKINS 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS | NORTH | 1973 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
B M DAVIS 1 |  | B_DAVIS_B_DAVIG1 | NUECES | GAS | SOUTH | 1974 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335
B M DAVIS 2 |  | B_DAVIS_B_DAVIG2 | NUECES | GAS | SOUTH | 1976 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
B M DAVIS 3 |  | B_DAVIS_B_DAVIG3 | NUECES | GAS | SOUTH | 2010 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
B M DAVIS 4 |  | B_DAVIS_B_DAVIG4 | NUECES | GAS | SOUTH | 2010 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
BASTROP ENERGY CENTER 1 |  | BASTEN_GTG1100 | BASTROP | GAS | SOUTH | 2002 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
BASTROP ENERGY CENTER 2 |  | BASTEN_GTG2100 | BASTROP | GAS | SOUTH | 2002 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
BASTROP ENERGY CENTER 3 |  | BASTEN_ST0100 | BASTROP | GAS | SOUTH | 2002 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234
BOSQUE COUNTY PEAKING 1 |  | BOSQUESW_BSQSU_1 | BOSQUE | GAS | NORTH | 2000 | 166.6 | 166.6 | 166.6 | 166.6 | 166.6 | 166.6 | 166.6 | 166.6 | 166.6 | 166.6
BOSQUE COUNTY PEAKING 2 |  | BOSQUESW_BSQSU_2 | BOSQUE | GAS | NORTH | 2000 | 166.6 | 166.6 | 166.6 | 166.6 | 166.6 | 166.6 | 166.6 | 166.6 | 166.6 | 166.6
BOSQUE COUNTY PEAKING 3 |  | BOSQUESW_BSQSU_3 | BOSQUE | GAS | NORTH | 2001 | 168.5 | 168.5 | 168.5 | 168.5 | 168.5 | 168.5 | 168.5 | 168.5 | 168.5 | 168.5
BOSQUE COUNTY PEAKING 4 |  | BOSQUESW_BSQSU_4 | BOSQUE | GAS | NORTH | 2001 | 85.2 | 85.2 | 85.2 | 85.2 | 85.2 | 85.2 | 85.2 | 85.2 | 85.2 | 85.2
BOSQUE COUNTY UNIT 5 |  | BOSQUESW_BSQSU_5 | BOSQUE | GAS | NORTH | 2009 | 200.7 | 200.7 | 200.7 | 200.7 | 200.7 | 200.7 | 200.7 | 200.7 | 200.7 | 200.7
BRAZOS VALLEY 1 |  | BVE_UNIT1 | FORT BEND | GAS | HOUSTON | 2003 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168
BRAZOS VALLEY 2 |  | BVE_UNIT2 | FORT BEND | GAS | HOUSTON | 2003 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168
BRAZOS VALLEY 3 |  | BVE_UNIT3 | FORT BEND | GAS | HOUSTON | 2003 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270
CALENERGY (FALCON SEABOARD) 1 |  | FLCNS_UNIT1 | HOWARD | GAS | WEST | 1987 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5
CALENERGY (FALCON SEABOARD) 2 |  | FLCNS_UNIT2 | HOWARD | GAS | WEST | 1987 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5
CALENERGY (FALCON SEABOARD) 3 |  | FLCNS_UNIT3 | HOWARD | GAS | WEST | 1988 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
CEDAR BAYOU 1 |  | CBY_CBY_G1 | CHAMBERS | GAS | HOUSTON | 1970 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745 | 745
CEDAR BAYOU 2 |  | CBY_CBY_G2 | CHAMBERS | GAS | HOUSTON | 1972 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749
CEDAR BAYOU 4 |  | CBY4_CT41 | CHAMBERS | GAS | HOUSTON | 2009 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173
CEDAR BAYOU 5 |  | CBY4_CT42 | CHAMBERS | GAS | HOUSTON | 2009 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173
CEDAR BAYOU 6 |  | CBY4_ST04 | CHAMBERS | GAS | HOUSTON | 2009 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186
COLORADO BEND ENERGY CENTER |  | CBEC_GT1 | WHARTON | GAS | HOUSTON | 2007 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88
COLORADO BEND ENERGY CENTER |  | CBEC_GT2 | WHARTON | GAS | HOUSTON | 2007 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
COLORADO BEND ENERGY CENTER |  | CBEC_GT3 | WHARTON | GAS | HOUSTON | 2008 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88
COLORADO BEND ENERGY CENTER |  | CBEC_GT4 | WHARTON | GAS | HOUSTON | 2008 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83
COLORADO BEND ENERGY CENTER |  | CBEC_STG1 | WHARTON | GAS | HOUSTON | 2007 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105
COLORADO BEND ENERGY CENTER |  | CBEC_STG2 | WHARTON | GAS | HOUSTON | 2008 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108
CVC CHANNELVIEW 1 |  | CVC_CVC_G1 | HARRIS | GAS | HOUSTON | 2008 | 157.8 | 157.8 | 157.8 | 157.8 | 157.8 | 157.8 | 157.8 | 157.8 | 157.8 | 157.8
CVC CHANNELVIEW 2 |  | CVC_CVC_G2 | HARRIS | GAS | HOUSTON | 2008 | 166.5 | 166.5 | 166.5 | 166.5 | 166.5 | 166.5 | 166.5 | 166.5 | 166.5 | 166.5
CVC CHANNELVIEW 3 |  | CVC_CVC_G3 | HARRIS | GAS | HOUSTON | 2008 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8
CVC CHANNELVIEW 5 |  | CVC_CVC_G5 | HARRIS | GAS | HOUSTON | 2008 | 132.9 | 132.9 | 132.9 | 132.9 | 132.9 | 132.9 | 132.9 | 132.9 | 132.9 | 132.9
DANSBY 1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS | NORTH | 1978 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
DANSBY 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS | NORTH | 2004 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
DANSBY 3 |  | DANSBY_DANSBYG3 | BRAZOS | GAS | NORTH | 2010 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
DECKER CREEK 1 |  | DECKER_DPG1 | TRAVIS | GAS | SOUTH | 1971 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
DECKER CREEK 2 |  | DECKER_DPG2 | TRAVIS | GAS | SOUTH | 1978 | 428 | 428 | 428 | 428 | 428 | 428 | 428 | 428 | 428 | 428
DECKER CREEK G1 |  | DECKER_DPGT_1 | TRAVIS | GAS | SOUTH | 1989 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
DECKER CREEK G2 |  | DECKER_DPGT_2 | TRAVIS | GAS | SOUTH | 1989 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
DECKER CREEK G3 |  | DECKER_DPGT_3 | TRAVIS | GAS | SOUTH | 1989 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
DECKER CREEK G4 |  | DECKER_DPGT_4 | TRAVIS | GAS | SOUTH | 1989 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
DECORDOVA A |  | DCSES_CT10 | HOOD | GAS | NORTH | 2010 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
DECORDOVA B |  | DCSES_CT20 | HOOD | GAS | NORTH | 2010 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
DECORDOVA C |  | DCSES_CT30 | HOOD | GAS | NORTH | 2010 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
DECORDOVA D |  | DCSES_CT40 | HOOD | GAS | NORTH | 2010 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77
DEER PARK ENERGY CENTER 1 |  | DDPEC_GT1 | HARRIS | GAS | Houston | 2002 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
DEER PARK ENERGY CENTER 2 |  | DDPEC_GT2 | HARRIS | GAS | Houston | 2002 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215
DEER PARK ENERGY CENTER 3 |  | DDPEC_GT3 | HARRIS | GAS | Houston | 2002 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
DEER PARK ENERGY CENTER 4 |  | DDPEC_GT4 | HARRIS | GAS | Houston | 2002 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215
DEER PARK ENERGY CENTER S |  | DDPEC_ST1 | HARRIS | GAS | Houston | 2002 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290
ENNIS POWER STATION 1 |  | ETCCS_UNIT1 | ELLIS | GAS | NORTH | 2002 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127
ENNIS POWER STATION 2 |  | ETCCS_CT1 | ELLIS | GAS | NORTH | 2002 | 231 | 231 | 231 | 231 | 231 | 231 | 231 | 231 | 231 | 231
EXTEX LA PORTE PWR STN (AIRPRO) 1 |  | AZ_AZ_G1 | HARRIS | GAS | HOUSTON | 2009 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
EXTEX LA PORTE PWR STN (AIRPRO) 2 |  | AZ_AZ_G2 | HARRIS | GAS | HOUSTON | 2009 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
EXTEX LA PORTE PWR STN (AIRPRO) 3 |  | AZ_AZ_G3 | HARRIS | GAS | HOUSTON | 2009 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
EXTEX LA PORTE PWR STN (AIRPRO) 4 |  | AZ_AZ_G4 | HARRIS | GAS | HOUSTON | 2009 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
FORNEY ENERGY CENTER GT11 |  | FRNYPP_GT11 | KAUFMAN | GAS | NORTH | 2003 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6
FORNEY ENERGY CENTER GT12 |  | FRNYPP_GT12 | KAUFMAN | GAS | NORTH | 2003 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6
FORNEY ENERGY CENTER GT13 |  | FRNYPP_GT13 | KAUFMAN | GAS | NORTH | 2003 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6
FORNEY ENERGY CENTER GT21 |  | FRNYPP_GT21 | KAUFMAN | GAS | NORTH | 2003 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6
FORNEY ENERGY CENTER GT22 |  | FRNYPP_GT22 | KAUFMAN | GAS | NORTH | 2003 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6
FORNEY ENERGY CENTER GT23 |  | FRNYPP_GT23 | KAUFMAN | GAS | NORTH | 2003 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6 | 191.6
FORNEY ENERGY CENTER STG10 |  | FRNYPP_ST10 | KAUFMAN | GAS | NORTH | 2003 | 401.2 | 401.2 | 401.2 | 401.2 | 401.2 | 401.2 | 401.2 | 401.2 | 401.2 | 401.2
FORNEY ENERGY CENTER STG20 |  | FRNYPP_ST20 | KAUFMAN | GAS | NORTH | 2003 | 401.2 | 401.2 | 401.2 | 401.2 | 401.2 | 401.2 | 401.2 | 401.2 | 401.2 | 401.2
FREESTONE ENERGY CENTER 1 |  | FREC_GT1 | FREESTONE | GAS | NORTH | 2002 | 160.73 | 160.73 | 160.73 | 160.73 | 160.73 | 160.73 | 160.73 | 160.73 | 160.73 | 160.73
FREESTONE ENERGY CENTER 2 |  | FREC_GT2 | FREESTONE | GAS | NORTH | 2002 | 160.73 | 160.73 | 160.73 | 160.73 | 160.73 | 160.73 | 160.73 | 160.73 | 160.73 | 160.73
FREESTONE ENERGY CENTER 3 |  | FREC_ST3 | FREESTONE | GAS | NORTH | 2002 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8
FREESTONE ENERGY CENTER 4 |  | FREC_GT4 | FREESTONE | GAS | NORTH | 2002 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1
FREESTONE ENERGY CENTER 5 |  | FREC_GT5 | FREESTONE | GAS | NORTH | 2002 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1
FREESTONE ENERGY CENTER 6 |  | FREC_ST6 | FREESTONE | GAS | NORTH | 2002 | 179.68 | 179.68 | 179.68 | 179.68 | 179.68 | 179.68 | 179.68 | 179.68 | 179.68 | 179.68
FRONTERA 1 |  | FRONTERA_FRONTEG1 | HILDALGO | GAS | SOUTH | 1999 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170
FRONTERA 2 |  | FRONTERA_FRONTEG2 | HILDALGO | GAS | SOUTH | 1999 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170
FRONTERA 3 |  | FRONTERA_FRONTEG3 | HILDALGO | GAS | SOUTH | 2000 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184
GRAHAM 1 |  | GRSES_UNIT1 | YOUNG | GAS | WEST | 1960 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225
GRAHAM 2 |  | GRSES_UNIT2 | YOUNG | GAS | WEST | 1969 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390
GREENS BAYOU 5 |  | GBY_GBY_5 | HARRIS | GAS | HOUSTON | 1973 | 406 | 406 | 406 | 406 | 406 | 406 | 406 | 406 | 406 | 406
GREENS BAYOU 73 |  | GBY_GBYGT73 | HARRIS | GAS | HOUSTON | 1976 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
GREENS BAYOU 74 |  | GBY_GBYGT74 | HARRIS | GAS | HOUSTON | 1976 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
GREENS BAYOU 81 |  | GBY_GBYGT81 | HARRIS | GAS | HOUSTON | 1976 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
GREENS BAYOU 83 |  | GBY_GBYGT83 | HARRIS | GAS | HOUSTON | 1976 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64
GREENS BAYOU 84 |  | GBY_GBYGT84 | HARRIS | GAS | HOUSTON | 1976 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58
GREENVILLE ENGINE PLANT |  | STEAM_ENGINE_1 | HUNT | GAS | NORTH | 2010 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439
GREENVILLE ENGINE PLANT |  | STEAM_ENGINE_2 | HUNT | GAS | NORTH | 2010 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439
GREENVILLE ENGINE PLANT |  | STEAM_ENGINE_3 | HUNT | GAS | NORTH | 2010 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439 | 8.439
GUADALUPE GEN STN 1 |  | GUADG_GAS1 | GUADALUPE | GAS | SOUTH | 2000 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
GUADALUPE GEN STN 2 |  | GUADG_GAS2 | GUADALUPE | GAS | SOUTH | 2000 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
GUADALUPE GEN STN 3 |  | GUADG_GAS3 | GUADALUPE | GAS | SOUTH | 2000 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
GUADALUPE GEN STN 4 |  | GUADG_GAS4 | GUADALUPE | GAS | SOUTH | 2000 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
GUADALUPE GEN STN 5 |  | GUADG_STM5 | GUADALUPE | GAS | SOUTH | 2000 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
GUADALUPE GEN STN 6 |  | GUADG_STM6 | GUADALUPE | GAS | SOUTH | 2000 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
HANDLEY 3 |  | HLSES_UNIT3 | TARRANT | GAS | NORTH | 1963 | 395 | 395 | 395 | 395 | 395 | 395 | 395 | 395 | 395 | 395
HANDLEY 4 |  | HLSES_UNIT4 | TARRANT | GAS | NORTH | 1976 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435
HANDLEY 5 |  | HLSES_UNIT5 | TARRANT | GAS | NORTH | 1977 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435
HAYS ENERGY FACILITY 1 |  | HAYSEN_HAYSENG1 | HAYS | GAS | SOUTH | 2002 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237
HAYS ENERGY FACILITY 2 |  | HAYSEN_HAYSENG2 | HAYS | GAS | SOUTH | 2002 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237
HAYS ENERGY FACILITY 3 |  | HAYSEN_HAYSENG3 | HAYS | GAS | SOUTH | 2002 | 247 | 247 | 247 | 247 | 247 | 247 | 247 | 247 | 247 | 247
HAYS ENERGY FACILITY 4 |  | HAYSEN_HAYSENG4 | HAYS | GAS | SOUTH | 2002 | 247 | 247 | 247 | 247 | 247 | 247 | 247 | 247 | 247 | 247
HIDALGO 1 |  | DUKE_DUKE_GT1 | HILDALGO | GAS | SOUTH | 2000 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
HIDALGO 2 |  | DUKE_DUKE_GT2 | HILDALGO | GAS | SOUTH | 2000 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
HIDALGO 3 |  | DUKE_DUKE_ST1 | HILDALGO | GAS | SOUTH | 2000 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176
JACK COUNTY GENFACILITY 2 |  | JCKCNTY2_CT3 | JACK | GAS | NORTH | 2011 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
JACK COUNTY GENFACILITY 2 |  | JCKCNTY2_CT4 | JACK | GAS | NORTH | 2011 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
JACK COUNTY GENFACILITY 2 |  | JCKCNTY2_ST2 | JACK | GAS | NORTH | 2011 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310
JACK COUNTY GENFACILITY 1 |  | JACKCNTY_CT1 | JACK | GAS | NORTH | 2005 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
JACK COUNTY GENFACILITY 1 |  | JACKCNTY_CT2 | JACK | GAS | NORTH | 2005 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
JACK COUNTY GENFACILITY 1 |  | JACKCNTY_STG | JACK | GAS | NORTH | 2005 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310
JOHNSON COUNTY GENFACILITY 1 |  | TEN_CT1 | JOHNSON | GAS | NORTH | 1997 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177
JOHNSON COUNTY GENFACILITY 2 |  | TEN_STG | JOHNSON | GAS | NORTH | 1997 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106
LAKE HUBBARD 1 |  | LHSES_UNIT1 | DALLAS | GAS | NORTH | 1970 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392
LAKE HUBBARD 2 |  | LH2SES_UNIT2 | DALLAS | GAS | NORTH | 2011 | 515 | 515 | 515 | 515 | 515 | 515 | 515 | 515 | 515 | 515
LAMAR POWER PROJECT CT11 |  | LPCCS_CT11 | LAMAR | GAS | NORTH | 2000 | 176.85 | 176.85 | 176.85 | 176.85 | 176.85 | 176.85 | 176.85 | 176.85 | 176.85 | 176.85
LAMAR POWER PROJECT CT12 |  | LPCCS_CT12 | LAMAR | GAS | NORTH | 2000 | 176.85 | 176.85 | 176.85 | 176.85 | 176.85 | 176.85 | 176.85 | 176.85 | 176.85 | 176.85
LAMAR POWER PROJECT CT21 |  | LPCCS_CT21 | LAMAR | GAS | NORTH | 2000 | 176.85 | 176.85 | 176.85 | 176.85 | 176.85 | 176.85 | 176.85 | 176.85 | 176.85 | 176.85
LAMAR POWER PROJECT CT22 |  | LPCCS_CT22 | LAMAR | GAS | NORTH | 2000 | 176.85 | 176.85 | 176.85 | 176.85 | 176.85 | 176.85 | 176.85 | 176.85 | 176.85 | 176.85
LAMAR POWER PROJECT STG1 |  | LPCCS_UNIT1 | LAMAR | GAS | NORTH | 2000 | 195.3 | 195.3 | 195.3 | 195.3 | 195.3 | 195.3 | 195.3 | 195.3 | 195.3 | 195.3
LAMAR POWER PROJECT STG2 |  | LPCCS_UNIT2 | LAMAR | GAS | NORTH | 2000 | 195.3 | 195.3 | 195.3 | 195.3 | 195.3 | 195.3 | 195.3 | 195.3 | 195.3 | 195.3
LAREDO PEAKING 4 |  | LARDVFTN_G4 | WEBB | GAS | SOUTH | 2008 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5
LAREDO PEAKING 5 |  | LARDVFTN_G5 | WEBB | GAS | SOUTH | 2008 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5
LEON CREEK PEAKING 1 |  | LEON_CRK_LCPCT1 | BEXAR | GAS | SOUTH | 2004 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
LEON CREEK PEAKING 2 |  | LEON_CRK_LCPCT2 | BEXAR | GAS | SOUTH | 2004 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
LEON CREEK PEAKING 3 |  | LEON_CRK_LCPCT3 | BEXAR | GAS | SOUTH | 2004 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
LEON CREEK PEAKING 4 |  | LEON_CRK_LCPCT4 | BEXAR | GAS | SOUTH | 2004 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
LOST PINES 1 |  | LOSTPI_LOSTPGT1 | BASTROP | GAS | SOUTH | 2001 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183
LOST PINES 2 |  | LOSTPI_LOSTPGT2 | BASTROP | GAS | SOUTH | 2001 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183
LOST PINES 3 |  | LOSTPI_LOSTPST1 | BASTROP | GAS | SOUTH | 2001 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192
MAGIC VALLEY 1 |  | NEDIN_NEDIN_G1 | HIDALGO | GAS | SOUTH | 2001 | 218.58 | 218.58 | 218.58 | 218.58 | 218.58 | 218.58 | 218.58 | 218.58 | 218.58 | 218.58
MAGIC VALLEY 2 |  | NEDIN_NEDIN_G2 | HIDALGO | GAS | SOUTH | 2001 | 218.58 | 218.58 | 218.58 | 218.58 | 218.58 | 218.58 | 218.58 | 218.58 | 218.58 | 218.58
MAGIC VALLEY 3 |  | NEDIN_NEDIN_G3 | HIDALGO | GAS | SOUTH | 2001 | 257.85 | 257.85 | 257.85 | 257.85 | 257.85 | 257.85 | 257.85 | 257.85 | 257.85 | 257.85
MIDLOTHIAN 1 |  | MDANP_CT1 | ELLIS | GAS | NORTH | 2001 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237
MIDLOTHIAN 2 |  | MDANP_CT2 | ELLIS | GAS | NORTH | 2001 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237
MIDLOTHIAN 3 |  | MDANP_CT3 | ELLIS | GAS | NORTH | 2001 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237
MIDLOTHIAN 4 |  | MDANP_CT4 | ELLIS | GAS | NORTH | 2001 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237
MIDLOTHIAN 5 |  | MDANP_CT5 | ELLIS | GAS | NORTH | 2002 | 247 | 247 | 247 | 247 | 247 | 247 | 247 | 247 | 247 | 247
MIDLOTHIAN 6 |  | MDANP_CT6 | ELLIS | GAS | NORTH | 2002 | 247 | 247 | 247 | 247 | 247 | 247 | 247 | 247 | 247 | 247
MORGAN CREEK A |  | MGSES_CT1 | MITCHELL | GAS | WEST | 1988 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
MORGAN CREEK B |  | MGSES_CT2 | MITCHELL | GAS | WEST | 1988 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
MORGAN CREEK C |  | MGSES_CT3 | MITCHELL | GAS | WEST | 1988 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
MORGAN CREEK D |  | MGSES_CT4 | MITCHELL | GAS | WEST | 1988 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
MORGAN CREEK E |  | MGSES_CT5 | MITCHELL | GAS | WEST | 1988 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
MORGAN CREEK F |  | MGSES_CT6 | MITCHELL | GAS | WEST | 1988 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
MOUNTAIN CREEK 6 |  | MCSES_UNIT6 | DALLAS | GAS | NORTH | 1956 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122
MOUNTAIN CREEK 7 |  | MCSES_UNIT7 | DALLAS | GAS | NORTH | 1958 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118
MOUNTAIN CREEK 8 |  | MCSES_UNIT8 | DALLAS | GAS | NORTH | 1967 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568
NUECES BAY 7 |  | NUECES_B_NUECESG7 | NUECES | GAS | SOUTH | 1972 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
NUECES BAY 8 |  | NUECES_B_NUECESG8 | NUECES | GAS | SOUTH | 2010 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
NUECES BAY 9 |  | NUECES_B_NUECESG9 | NUECES | GAS | SOUTH | 2010 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
O W SOMMERS 1 |  | CALAVERS_OWS1 | BEXAR | GAS | SOUTH | 1972 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
O W SOMMERS 2 |  | CALAVERS_OWS2 | BEXAR | GAS | SOUTH | 1974 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
ODESSA-ECTOR GEN STN C11 |  | OECCS_CT11 | ECTOR | GAS | WEST | 2001 | 162.6 | 162.6 | 162.6 | 162.6 | 162.6 | 162.6 | 162.6 | 162.6 | 162.6 | 162.6
ODESSA-ECTOR GEN STN C12 |  | OECCS_CT12 | ECTOR | GAS | WEST | 2001 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2
ODESSA-ECTOR GEN STN C21 |  | OECCS_CT21 | ECTOR | GAS | WEST | 2001 | 155.8 | 155.8 | 155.8 | 155.8 | 155.8 | 155.8 | 155.8 | 155.8 | 155.8 | 155.8
ODESSA-ECTOR GEN STN C22 |  | OECCS_CT22 | ECTOR | GAS | WEST | 2001 | 153.3 | 153.3 | 153.3 | 153.3 | 153.3 | 153.3 | 153.3 | 153.3 | 153.3 | 153.3
ODESSA-ECTOR GEN STN ST1 |  | OECCS_UNIT1 | ECTOR | GAS | WEST | 2001 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216
ODESSA-ECTOR GEN STN ST2 |  | OECCS_UNIT2 | ECTOR | GAS | WEST | 2001 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216
PARIS ENERGY CENTER 1 |  | TNSKA_GT1 | LAMAR | GAS | NORTH | 1989 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87
PARIS ENERGY CENTER 2 |  | TNSKA_GT2 | LAMAR | GAS | NORTH | 1989 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87
PARIS ENERGY CENTER 3 |  | TNSKA_STG | LAMAR | GAS | NORTH | 1990 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89
PASGEN |  | PSG_PSG_GT2 | HARRIS | GAS | HOUSTON | 2000 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176
PASGEN |  | PSG_PSG_GT3 | HARRIS | GAS | HOUSTON | 2000 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176 | 176
PASGEN |  | PSG_PSG_ST2 | HARRIS | GAS | HOUSTON | 2000 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
PEARSALL 1 |  | PEARSALL_PEARS_1 | FRIO | GAS | SOUTH | 1961 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
PEARSALL 2 |  | PEARSALL_PEARS_2 | FRIO | GAS | SOUTH | 1961 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
PEARSALL 3 |  | PEARSALL_PEARS_3 | FRIO | GAS | SOUTH | 1961 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
PEARSALL ENGINE PLANT |  | PEARSAL2_AGR_A | FRIO | GAS | SOUTH | 2012 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64
PEARSALL ENGINE PLANT |  | PEARSAL2_AGR_B | FRIO | GAS | SOUTH | 2012 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64
PEARSALL ENGINE PLANT |  | PEARSAL2_AGR_C | FRIO | GAS | SOUTH | 2012 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64
PEARSALL ENGINE PLANT |  | PEARSAL2_AGR_D | FRIO | GAS | SOUTH | 2012 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64 | 50.64
PERMIAN BASIN A |  | PB2SES_CT1 | WARD | GAS | WEST | 1988 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71
PERMIAN BASIN B |  | PB2SES_CT2 | WARD | GAS | WEST | 1988 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71
PERMIAN BASIN C |  | PB2SES_CT3 | WARD | GAS | WEST | 1988 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
PERMIAN BASIN D |  | PB2SES_CT4 | WARD | GAS | WEST | 1990 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
PERMIAN BASIN E |  | PB2SES_CT5 | WARD | GAS | WEST | 1990 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
POWERLANE PLANT 1 |  | STEAM1A_STEAM_1 | HUNT | GAS | NORTH | 2009 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
POWERLANE PLANT 2 |  | STEAM_STEAM_2 | HUNT | GAS | NORTH | 1967 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
POWERLANE PLANT 3 |  | STEAM_STEAM_3 | HUNT | GAS | NORTH | 1978 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41
QUAIL RUN ENERGY GT1 |  | QALSW_GT2 | ECTOR | GAS | WEST | 2007 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86
QUAIL RUN ENERGY GT2 |  | QALSW_GT3 | ECTOR | GAS | WEST | 2008 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
QUAIL RUN ENERGY GT3 |  | QALSW_STG1 | ECTOR | GAS | WEST | 2007 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
QUAIL RUN ENERGY GT4 |  | QALSW_STG2 | ECTOR | GAS | WEST | 2008 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
QUAIL RUN ENERGY STG1 |  | QALSW_GT1 | ECTOR | GAS | WEST | 2007 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
QUAIL RUN ENERGY STG2 |  | QALSW_GT4 | ECTOR | GAS | WEST | 2008 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
R W MILLER 1 |  | MIL_MILLERG1 | PALO PINTO | GAS | NORTH | 2000 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
R W MILLER 2 |  | MIL_MILLERG2 | PALO PINTO | GAS | NORTH | 2000 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
R W MILLER 3 |  | MIL_MILLERG3 | PALO PINTO | GAS | NORTH | 2000 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208
R W MILLER 4 |  | MIL_MILLERG4 | PALO PINTO | GAS | NORTH | 2000 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115
R W MILLER 5 |  | MIL_MILLERG5 | PALO PINTO | GAS | NORTH | 2000 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115
RAY OLINGER 1 |  | OLINGR_OLING_1 | COLLIN | GAS | NORTH | 1967 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
RAY OLINGER 2 |  | OLINGR_OLING_2 | COLLIN | GAS | NORTH | 1971 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107
RAY OLINGER 3 |  | OLINGR_OLING_3 | COLLIN | GAS | NORTH | 1975 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146
RAY OLINGER 4 |  | OLINGR_OLING_4 | COLLIN | GAS | NORTH | 2001 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
RAYBURN 1 |  | RAYBURN_RAYBURG1 | VICTORIA | GAS | SOUTH | 1963 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5
RAYBURN 10 |  | RAYBURN_RAYBURG10 | VICTORIA | GAS | SOUTH | 2003 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
RAYBURN 2 |  | RAYBURN_RAYBURG2 | VICTORIA | GAS | SOUTH | 1963 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5
RAYBURN 7 |  | RAYBURN_RAYBURG7 | VICTORIA | GAS | SOUTH | 2003 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
RAYBURN 8 |  | RAYBURN_RAYBURG8 | VICTORIA | GAS | SOUTH | 2003 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51
RAYBURN 9 |  | RAYBURN_RAYBURG9 | VICTORIA | GAS | SOUTH | 2003 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
RIO NOGALES 1 |  | RIONOG_CT1 | GUADALUPE | GAS | SOUTH | 2002 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175
RIO NOGALES 2 |  | RIONOG_CT2 | GUADALUPE | GAS | SOUTH | 2002 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175
RIO NOGALES 3 |  | RIONOG_CT3 | GUADALUPE | GAS | SOUTH | 2002 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175
RIO NOGALES 4 |  | RIONOG_ST1 | GUADALUPE | GAS | SOUTH | 2002 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323
SAN JACINTO SES 1 |  | SJS_SJS_G1 | HARRIS | GAS | HOUSTON | 1995 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
SAN JACINTO SES 2 |  | SJS_SJS_G2 | HARRIS | GAS | HOUSTON | 1995 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
SANDHILL ENERGY CENTER 1 |  | SANDHSYD_SH1 | TRAVIS | GAS | SOUTH | 2001 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SANDHILL ENERGY CENTER 2 |  | SANDHSYD_SH2 | TRAVIS | GAS | SOUTH | 2001 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SANDHILL ENERGY CENTER 3 |  | SANDHSYD_SH3 | TRAVIS | GAS | SOUTH | 2001 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SANDHILL ENERGY CENTER 4 |  | SANDHSYD_SH4 | TRAVIS | GAS | SOUTH | 2001 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SANDHILL ENERGY CENTER 5A |  | SANDHSYD_SH_5A | TRAVIS | GAS | SOUTH | 2004 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170
SANDHILL ENERGY CENTER 5C |  | SANDHSYD_SH_5C | TRAVIS | GAS | SOUTH | 2004 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
SANDHILL ENERGY CENTER 6 |  | SANDHSYD_SH6 | TRAVIS | GAS | SOUTH | 2010 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SANDHILL ENERGY CENTER 7 |  | SANDHSYD_SH7 | TRAVIS | GAS | SOUTH | 2010 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SILAS RAY 10 |  | SILASRAY_SILAS_10 | CAMERON | GAS | SOUTH | 2004 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
SILAS RAY 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS | SOUTH | 1962 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
SILAS RAY 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS | SOUTH | 1996 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49
SIM GIDEON 1 |  | GIDEON_GIDEONG1 | BASTROP | GAS | SOUTH | 1965 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130
SIM GIDEON 2 |  | GIDEON_GIDEONG2 | BASTROP | GAS | SOUTH | 1968 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135
SIM GIDEON 3 |  | GIDEON_GIDEONG3 | BASTROP | GAS | SOUTH | 1972 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340
SPENCER 4 |  | SPNCER_SPNCE_4 | DENTON | GAS | NORTH | 1966 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
SPENCER 5 |  | SPNCER_SPNCE_5 | DENTON | GAS | NORTH | 1973 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
STRYKER CREEK 1 |  | SCSES_UNIT1A | CHEROKEE | GAS | NORTH | 1958 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
STRYKER CREEK 2 |  | SCSES_UNIT2 | CHEROKEE | GAS | NORTH | 1965 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502
T H WHARTON 3 |  | THW_THWST_3 | HARRIS | GAS | HOUSTON | 1974 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104
T H WHARTON 31 |  | THW_THWGT31 | HARRIS | GAS | HOUSTON | 1972 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON 32 |  | THW_THWGT32 | HARRIS | GAS | HOUSTON | 1972 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON 33 |  | THW_THWGT33 | HARRIS | GAS | HOUSTON | 1972 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON 34 |  | THW_THWGT34 | HARRIS | GAS | HOUSTON | 1972 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON 4 |  | THW_THWST_4 | HARRIS | GAS | HOUSTON | 1974 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104
T H WHARTON 41 |  | THW_THWGT41 | HARRIS | GAS | HOUSTON | 1972 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON 42 |  | THW_THWGT42 | HARRIS | GAS | HOUSTON | 1972 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON 43 |  | THW_THWGT43 | HARRIS | GAS | HOUSTON | 1974 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON 44 |  | THW_THWGT44 | HARRIS | GAS | HOUSTON | 1974 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON 51 |  | THW_THWGT51 | HARRIS | GAS | HOUSTON | 1975 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON 52 |  | THW_THWGT52 | HARRIS | GAS | HOUSTON | 1975 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON 53 |  | THW_THWGT53 | HARRIS | GAS | HOUSTON | 1975 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON 54 |  | THW_THWGT54 | HARRIS | GAS | HOUSTON | 1975 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON 55 |  | THW_THWGT55 | HARRIS | GAS | HOUSTON | 1975 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON 56 |  | THW_THWGT56 | HARRIS | GAS | HOUSTON | 1975 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON G1 |  | THW_THWGT_1 | HARRIS | GAS | HOUSTON | 1967 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
TEXAS CITY 1 |  | TXCTY_CTA | GALVESTON | GAS | HOUSTON | 2000 | 102.38 | 102.38 | 102.38 | 102.38 | 102.38 | 102.38 | 102.38 | 102.38 | 102.38 | 102.38
TEXAS CITY 2 |  | TXCTY_CTB | GALVESTON | GAS | HOUSTON | 2000 | 102.38 | 102.38 | 102.38 | 102.38 | 102.38 | 102.38 | 102.38 | 102.38 | 102.38 | 102.38
TEXAS CITY 3 |  | TXCTY_CTC | GALVESTON | GAS | HOUSTON | 2000 | 102.38 | 102.38 | 102.38 | 102.38 | 102.38 | 102.38 | 102.38 | 102.38 | 102.38 | 102.38
TEXAS CITY 4 |  | TXCTY_ST | GALVESTON | GAS | HOUSTON | 2000 | 131.49 | 131.49 | 131.49 | 131.49 | 131.49 | 131.49 | 131.49 | 131.49 | 131.49 | 131.49
TEXAS GULF SULPHUR |  | TGF_TGFGT_1 | WHARTON | GAS | HOUSTON | 1985 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89
TRINIDAD 6 |  | TRSES_UNIT6 | HENDERSON | GAS | NORTH | 2011 | 226 | 226 | 226 | 226 | 226 | 226 | 226 | 226 | 226 | 226
V H BRAUNIG 1 |  | BRAUNIG_VHB1 | BEXAR | GAS | SOUTH | 1966 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
V H BRAUNIG 2 |  | BRAUNIG_VHB2 | BEXAR | GAS | SOUTH | 1968 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230
V H BRAUNIG 3 |  | BRAUNIG_VHB3 | BEXAR | GAS | SOUTH | 1970 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412 | 412
V H BRAUNIG 5 |  | BRAUNIG_VHB6CT5 | BEXAR | GAS | SOUTH | 2009 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
V H BRAUNIG 6 |  | BRAUNIG_VHB6CT6 | BEXAR | GAS | SOUTH | 2009 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
V H BRAUNIG 7 |  | BRAUNIG_VHB6CT7 | BEXAR | GAS | SOUTH | 2009 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
V H BRAUNIG 8 |  | BRAUNIG_VHB6CT8 | BEXAR | GAS | SOUTH | 2009 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
VICTORIA POWER STATION 5 |  | VICTORIA_VICTORG5 | VICTORIA | GAS | SOUTH | 2009 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132
VICTORIA POWER STATION 6 |  | VICTORIA_VICTORG6 | VICTORIA | GAS | SOUTH | 2009 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168
W A PARISH 1 |  | WAP_WAP_G1 | FORT BEND | GAS | HOUSTON | 1958 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
W A PARISH 2 |  | WAP_WAP_G2 | FORT BEND | GAS | HOUSTON | 1958 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
W A PARISH 3 |  | WAP_WAP_G3 | FORT BEND | GAS | HOUSTON | 1961 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258
W A PARISH 4 |  | WAP_WAP_G4 | FORT BEND | GAS | HOUSTON | 1968 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552
W A PARISH T1 |  | WAP_WAPGT_1 | FORT BEND | GAS | HOUSTON | 1967 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
WICHITA FALLS 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS | WEST | 1987 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
WICHITA FALLS 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS | WEST | 1987 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
WICHITA FALLS 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS | WEST | 1987 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
WICHITA FALLS 4 |  | WFCOGEN_UNIT4 | WICHITA | GAS | WEST | 1987 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
WINCHESTER POWER PARK 1 |  | WIPOPA_WPP_G1 | FAYETTE | GAS | SOUTH | 2009 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
WINCHESTER POWER PARK 2 |  | WIPOPA_WPP_G2 | FAYETTE | GAS | SOUTH | 2009 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
WINCHESTER POWER PARK 3 |  | WIPOPA_WPP_G3 | FAYETTE | GAS | SOUTH | 2009 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
WINCHESTER POWER PARK 4 |  | WIPOPA_WPP_G4 | FAYETTE | GAS | SOUTH | 2009 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
WISE-TRACTEBEL POWER PROJ. 1 |  | WCPP_CT1 | WISE | GAS | NORTH | 2004 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275
WISE-TRACTEBEL POWER PROJ. 2 |  | WCPP_CT2 | WISE | GAS | NORTH | 2004 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275
WISE-TRACTEBEL POWER PROJ. 3 |  | WCPP_ST1 | WISE | GAS | NORTH | 2004 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290
WOLF HOLLOW POWER PROJ. 1 |  | WHCCS_CT1 | HOOD | GAS | NORTH | 2002 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249
WOLF HOLLOW POWER PROJ. 2 |  | WHCCS_CT2 | HOOD | GAS | NORTH | 2002 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249
WOLF HOLLOW POWER PROJ. 3 |  | WHCCS_STG | HOOD | GAS | NORTH | 2002 | 293 | 293 | 293 | 293 | 293 | 293 | 293 | 293 | 293 | 293
PETRO NOVA - WA PARISH |  | PNPI_GT2 | FORT BEND | GAS | HOUSTON | 2013 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88
COMANCHE PEAK 1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1235 | 1235 | 1235 | 1235 | 1235 | 1235 | 1235 | 1235 | 1235 | 1235
COMANCHE PEAK 2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1225 | 1225 | 1225 | 1225 | 1225 | 1225 | 1225 | 1225 | 1225 | 1225
SOUTH TEXAS 1 |  | STP_STP_G1 | MATAGORDA | NUCLEAR | SOUTH | 1988 | 1375 | 1375 | 1375 | 1375 | 1375 | 1375 | 1375 | 1375 | 1375 | 1375
SOUTH TEXAS 2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | SOUTH | 1989 | 1375 | 1375 | 1375 | 1375 | 1375 | 1375 | 1375 | 1375 | 1375 | 1375
NOTREES BATTERY |  | NWF_NBS | WINKLER/ECTOR | STORAGE | WEST | 2012 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7
AES DEEPWATER |  | APD_APD_PS1 | HARRIS | STORAGE | HOUSTON | 2010 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
WEBBERVILLE |  | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5
ACACIA SOLAR |  | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 9.99 | 9.99 | 9.99 | 9.99 | 9.99 | 9.99 | 9.99 | 9.99 | 9.99 | 9.99
OCI ALAMO 1 | 13INR0058 | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.183 | 39.183 | 39.183 | 39.183 | 39.183 | 39.183 | 39.183 | 39.183 | 39.183 | 39.183
BLUE WING 1 |  | DG_BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.56 | 7.56 | 7.56 | 7.56 | 7.56 | 7.56 | 7.56 | 7.56 | 7.56 | 7.56
BLUE WING 2 |  | DG_ELMEN_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3
SOMERSET 1 |  | DG_SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61 | 5.61
SOMERSET 2 |  | DG_SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95
SUNEDISON RABEL ROAD |  | DG_VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SUNEDISON VALLEY ROAD |  | DG_VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
NACOGDOCHES POWER |  | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105
LUFKIN BIOMASS |  | LFBIO_UNIT1 | ANGELINA | BIOMASS | NORTH | 2012 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
ALVIN |  | AV_DG1 | GALVESTON | BIOMASS | HOUSTON | 2002 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
AUSTIN LANDFILL GAS |  | DG_SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
COVEL GARDENS POWER STATION |  | DG_MEDIN_1UNIT | BEXAR | BIOMASS | SOUTH | 2005 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
DFW GAS RECOVERY |  | DG_BIO2_4UNITS | DENTON | BIOMASS | NORTH | 2009 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
DG_BIOENERGY PARTNERS |  | DG_BIOE_2UNITS | DENTON | BIOMASS | NORTH | 1988 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2
FW REGION GEN FACILITY |  | DG_RDLML_1UNIT | TARRANT | BIOMASS | NORTH | 2011 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
HUMBLE |  | HB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
LIBERTY |  | LB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 3.872 | 3.872 | 3.872 | 3.872 | 3.872 | 3.872 | 3.872 | 3.872 | 3.872 | 3.872
MCKINNEY LANDFILL |  | DG_MKNSW_2UNITS | COLLIN | BIOMASS | NORTH | 2011 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
MESQUITE CREEK ENERGY |  | DG_FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
SKYLINE LANDFILL GAS |  | DG_FERIS_4_UNITS | DALLAS | BIOMASS | NORTH | 2007 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
TRINITY BAY |  | TRN_DG1 | CHAMBERS | BIOMASS | HOUSTON | 2002 | 3.872 | 3.872 | 3.872 | 3.872 | 3.872 | 3.872 | 3.872 | 3.872 | 3.872 | 3.872
TRINITY OAKS LFG |  | DG_KLBRG_1UNIT | DALLAS | BIOMASS | NORTH | 2011 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
WALZEM ROAD |  | DG_WALZE_4UNITS | BEXAR | BIOMASS | SOUTH | 2002 | 9.78 | 9.78 | 9.78 | 9.78 | 9.78 | 9.78 | 9.78 | 9.78 | 9.78 | 9.78
WESTSIDE |  | DG_WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
KMAYBTO |  | DG_KMASB_1UNIT | WICHITA | BIOMASS | WEST | 2011 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125
Operational Capacity Total (Coal, Gas, Nuclear, Biomass, Solar) | [6 empty] | 64852.0991 | 64852.0991 | 64852.0991 | 64852.0991 | 64852.0991 | 64002.0991 | 64002.0991 | 64002.0991 | 64002.0991 | 64002.0991
Operational Resources (Hydro)
CANYON |  | CANYHY_CANYHYG1 | COMAL |  | SOUTH | 1989 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
EAGLE PASS HYDRO |  | EAGLE_HY_EAGLE_HY1 | MAVERICK |  | SOUTH | 2005 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
LAKEWOOD TAP |  | DG_LKWDT_2UNITS | GONZALES |  | SOUTH | 1931 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
LEWISVILLE |  | DG_LWSVL_1UNIT | DENTON |  | NORTH | 1991 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2
MCQUEENEY |  | DG_MCQUE_5UNITS | GUADALUPE |  | SOUTH | 1928 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7
SCHUMANSVILLE |  | DG_SCHUM_2UNITS | GUADALUPE |  | SOUTH | 1928 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6
AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE |  | SOUTH | 1983 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9
AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE |  | SOUTH | 1983 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9
AUSTIN 1 |  | AUSTPL_AUSTING1 | TRAVIS |  | SOUTH | 1940 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
AUSTIN 2 |  | AUSTPL_AUSTING2 | TRAVIS |  | SOUTH | 1940 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
BUCHANAN 1 |  | BUCHAN_BUCHANG1 | LLANO |  | SOUTH | 1938 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
BUCHANAN 2 |  | BUCHAN_BUCHANG2 | LLANO |  | SOUTH | 1938 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
BUCHANAN 3 |  | BUCHAN_BUCHANG3 | LLANO |  | SOUTH | 1950 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON |  | NORTH | 1944 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON |  | NORTH | 1948 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR |  | SOUTH | 1954 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR |  | SOUTH | 1954 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR |  | SOUTH | 1954 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
GRANITE SHOALS 1 |  | WIRTZ_WIRTZ_G1 | BURNET |  | SOUTH | 1951 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
GRANITE SHOALS 2 |  | WIRTZ_WIRTZ_G2 | BURNET |  | SOUTH | 1951 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
INKS 1 |  | INKSDA_INKS_G1 | LLANO |  | SOUTH | 1938 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
MARBLE FALLS 1 |  | MARBFA_MARBFAG1 | BURNET |  | SOUTH | 1951 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
MARBLE FALLS 2 |  | MARBFA_MARBFAG2 | BURNET |  | SOUTH | 1951 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
MARSHALL FORD 1 |  | MARSFO_MARSFOG1 | TRAVIS |  | SOUTH | 1941 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
MARSHALL FORD 2 |  | MARSFO_MARSFOG2 | TRAVIS |  | SOUTH | 1941 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
MARSHALL FORD 3 |  | MARSFO_MARSFOG3 | TRAVIS |  | SOUTH | 1941 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
WHITNEY DAM |  | WND_WHITNEY1 | BOSQUE |  | NORTH | 1953 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
WHITNEY 2 |  | WND_WHITNEY2 | BOSQUE |  | NORTH | 1953 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
Operational Capacity (Hydro) | [6 empty] | 540.7 | 540.7 | 540.7 | 540.7 | 540.7 | 540.7 | 540.7 | 540.7 | 540.7 | 540.7
Hydro Capacity Contribution (Ave. maximum capability for Top 20 Hours) |  |  |  | HYDRO |  |  | 446.2 | 446.2 | 446.2 | 446.2 | 446.2 | 446.2 | 446.2 | 446.2 | 446.2 | 446.2
Operational Capacity Total (Including Hydro) | [6 empty] | 65298.2991 | 65298.2991 | 65298.2991 | 65298.2991 | 65298.2991 | 64448.2991 | 64448.2991 | 64448.2991 | 64448.2991 | 64448.2991
Private Use Network (PUN) Capacity Contribution (Average maximum capability Top 20 Hours) |  |  |  | GAS |  |  | 4474 | 4474 | 4474 | 4474 | 4474 | 4474 | 4474 | 4474 | 4474 | 4474
NEW PUN UNIT | 14INR0016 |  | HARRIS | GAS | HOUSTON | 2014 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194
Capacity from Private Use Networks | [6 empty] | 4668 | 4668 | 4668 | 4668 | 4668 | 4668 | 4668 | 4668 | 4668 | 4668
RMR Capacity Total | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DC-Ties
EAGLE PASS |  | DC_S | MAVERICK |  | SOUTH |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
EAST |  | DC_E | FANNIN |  | NORTH |  | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
LAREDO VFT |  | DC_L | WEBB |  | SOUTH |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
NORTH |  | DC_N | WILBARGER |  | WEST |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
SHARYLAND (RAILROAD) |  | DC_R | HILDALGO |  | SOUTH |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SHARYLAND (NEW RAILROAD TIE) |  | DC_R2 | HILDALGO |  | SOUTH |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
DC-Tie Capacity | [6 empty] | 1256 | 1256 | 1256 | 1256 | 1256 | 1256 | 1256 | 1256 | 1256 | 1256
DC-Ties Capacity Contribution (Ave. maximum capability for Top 20 Hours) |  |  |  | OTHER |  |  | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3
Switchable Resources
KIAMICHI ENERGY FACILITY 1CT101 |  | KMCHI_1CT101 | PITTSBURG | GAS | NORTH | 2003 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
KIAMICHI ENERGY FACILITY 1CT201 |  | KMCHI_1CT201 | PITTSBURG | GAS | NORTH | 2003 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
KIAMICHI ENERGY FACILITY 1ST |  | KMCHI_1ST | PITTSBURG | GAS | NORTH | 2003 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307
KIAMICHI ENERGY FACILITY 2CT101 |  | KMCHI_2CT101 | PITTSBURG | GAS | NORTH | 2003 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
KIAMICHI ENERGY FACILITY 2CT201 |  | KMCHI_2CT201 | PITTSBURG | GAS | NORTH | 2003 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
KIAMICHI ENERGY FACILITY 2ST |  | KMCHI_2ST | PITTSBURG | GAS | NORTH | 2003 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307
TENASKA-FRONTIER 1 |  | FTR_FTR_G1 | GRIMES | GAS | HOUSTON | 2000 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
TENASKA-FRONTIER 2 |  | FTR_FTR_G2 | GRIMES | GAS | HOUSTON | 2000 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
TENASKA-FRONTIER 3 |  | FTR_FTR_G3 | GRIMES | GAS | HOUSTON | 2000 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
TENASKA-FRONTIER 4 |  | FTR_FTR_G4 | GRIMES | GAS | HOUSTON | 2000 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
TENASKA-GATEWAY 1 |  | TGCCS_CT1 | RUSK | GAS | NORTH | 2001 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162
TENASKA-GATEWAY 2 |  | TGCCS_CT2 | RUSK | GAS | NORTH | 2001 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179
TENASKA-GATEWAY 3 |  | TGCCS_CT3 | RUSK | GAS | NORTH | 2001 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
TENASKA-GATEWAY 4 |  | TGCCS_UNIT4 | RUSK | GAS | NORTH | 2001 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389
Switchable Capacity Total | [6 empty] | 3178 | 3178 | 3178 | 3178 | 3178 | 3178 | 3178 | 3178 | 3178 | 3178
Wind Resources
ANACACHO WINDFARM |  | ANACACHO_ANA | KINNEY | WIND | SOUTH | 2012 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101
BARTON CHAPEL WIND |  | BRTSW_BCW1 | JACK | WIND | WEST | 2007 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
BOBCAT WIND |  | BCATWIND_WIND_1 | ARCHER | WIND | NORTH | 2012 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
BLUE SUMMIT WIND 5 | 12INR0075 | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND | WEST | 2012 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
BLUE SUMMIT WIND 6 | 12INR0075 | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND | WEST | 2012 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4
BUFFALO GAP WIND FARM 1 |  | BUFF_GAP_UNIT1 | TAYLOR | WIND | WEST | 2006 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6
BUFFALO GAP WIND FARM 2 |  | BUFF_GAP_UNIT2_1 | TAYLOR | WIND | WEST | 2007 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5
BUFFALO GAP WIND FARM 2 |  | BUFF_GAP_UNIT2_2 | TAYLOR | WIND | WEST | 2007 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117
BUFFALO GAP WIND FARM 3 |  | BUFF_GAP_UNIT3 | TAYLOR | WIND | WEST | 2008 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2
BULL CREEK WIND PLANT |  | BULLCRK_WND1 | BORDEN | WIND | WEST | 2009 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88
BULL CREEK WIND PLANT |  | BULLCRK_WND2 | BORDEN | WIND | WEST | 2009 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
CALLAHAN WIND |  | CALLAHAN_WND1 | CALLAHAN | WIND | WEST | 2004 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114
CAMP SPRINGS 1 |  | CSEC_CSECG1 | SCURRY | WIND | WEST | 2007 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5
CAMP SPRINGS 2 |  | CSEC_CSECG2 | SCURRY | WIND | WEST | 2007 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
CAPRICORN RIDGE WIND 1 |  | CAPRIDGE_CR1 | STERLING | WIND | WEST | 2007 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5 | 214.5
CAPRICORN RIDGE WIND 2 |  | CAPRIDGE_CR3 | STERLING | WIND | WEST | 2008 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186
CAPRICORN RIDGE WIND 3 |  | CAPRIDGE_CR2 | STERLING | WIND | WEST | 2007 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5
CAPRICORN RIDGE WIND 4 |  | CAPRIDG4_CR4 | COKE/STERLING | WIND | WEST | 2008 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5
CEDRO HILL WIND |  | CEDROHIL_CHW1 | WEBB | WIND | SOUTH | 2010 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
CHAMPION WIND FARM |  | CHAMPION_UNIT1 | NOLAN/MITCHELL | WIND | WEST | 2008 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5
DELAWARE MOUNTAIN WIND FARM |  | KUNITZ_WIND_NWP | CULBERSON | WIND | WEST | 1999 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5
DESERT SKY WIND FARM 1 |  | INDNENR_INDNENR | PECOS | WIND | WEST | 2002 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
DESERT SKY WIND FARM 2 |  | INDNENR_INDNENR_2 | PECOS | WIND | WEST | 2002 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5
ELBOW CREEK WIND PROJECT |  | ELB_ELBCREEK | HOWARD | WIND | WEST | 2008 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7
FOREST CREEK WIND FARM |  | MCDLD_FCW1 | GLASSCOCK | WIND | WEST | 2007 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2
GOAT WIND |  | GOAT_GOATWIND | STERLING | WIND | WEST | 2008 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
GOAT WIND 2 |  | GOAT_GOATWIN2 | STERLING | WIND | WEST | 2010 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6
GREEN MOUNTAIN ENERGY 1 |  | BRAZ_WND_WND1 | SCURRY/BORDEN | WIND | WEST | 2003 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99
GREEN MOUNTAIN ENERGY 2 |  | BRAZ_WND_WND2 | SCURRY/BORDEN | WIND | WEST | 2003 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
GULF WIND I |  | TGW_T1 | KENEDY | WIND | SOUTH | 2010 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
GULF WIND II |  | TGW_T2 | KENEDY | WIND | SOUTH | 2010 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
HACKBERRY WIND FARM |  | HWF_HWFG1 | SHACKELFORD | WIND | WEST | 2008 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5
HARBOR WIND |  | DG_NUECE_6UNITS | NUECES | WIND | SOUTH | 2012 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
HORSE HOLLOW WIND 1 |  | H_HOLLOW_WND1 | TAYLOR | WIND | WEST | 2005 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213
HORSE HOLLOW WIND 2 |  | HHOLLOW2_WIND1 | TAYLOR | WIND | WEST | 2006 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184
HORSE HOLLOW WIND 3 |  | HHOLLOW3_WND_1 | TAYLOR | WIND | WEST | 2006 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5
HORSE HOLLOW WIND 4 |  | HHOLLOW4_WND1 | TAYLOR | WIND | WEST | 2006 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115
INADALE WIND |  | INDL_INADALE1 | NOLAN | WIND | WEST | 2008 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6
INDIAN MESA WIND FARM |  | INDNNWP_INDNNWP | PECOS | WIND | WEST | 2001 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5
KING MOUNTAIN NE |  | KING_NE_KINGNE | UPTON | WIND | WEST | 2001 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3
KING MOUNTAIN NW |  | KING_NW_KINGNW | UPTON | WIND | WEST | 2001 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3
KING MOUNTAIN SE |  | KING_SE_KINGSE | UPTON | WIND | WEST | 2001 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3
KING MOUNTAIN SW |  | KING_SW_KINGSW | UPTON | WIND | WEST | 2001 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3
KUNITZ WIND |  | KUNITZ_WIND_LGE | CULBERSON | WIND | WEST | 1995 | 39.8 | 39.8 | 39.8 | 39.8 | 39.8 | 39.8 | 39.8 | 39.8 | 39.8 | 39.8
LANGFORD WIND POWER |  | LGD_LANGFORD | TOM GREEN | WIND | WEST | 2009 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
LORAINE WINDPARK I |  | LONEWOLF_G1 | MITCHELL | WIND | WEST | 2009 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5
LORAINE WINDPARK II |  | LONEWOLF_G2 | MITCHELL | WIND | WEST | 2009 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51
LORAINE WINDPARK III |  | LONEWOLF_G3 | MITCHELL | WIND | WEST | 2011 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5
LORAINE WINDPARK IV |  | LONEWOLF_G4 | MITCHELL | WIND | WEST | 2011 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
LOS VIENTOS WIND I |  | LV1_LV1A | WILLACY | WIND | SOUTH | 2013 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1
LOS VIENTOS WIND II |  | LV1_LV1B | WILLACY | WIND | SOUTH | 2013 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6
MAGIC VALLEY WIND |  | REDFISH_MV1A | WILLACY | WIND | SOUTH | 2012 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103
MAGIC VALLEY WIND |  | REDFISH_MV1B | WILLACY | WIND | SOUTH | 2012 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103
MCADOO WIND FARM |  | MWEC_G1 | DICKENS | WIND | WEST | 2008 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
MESQUITE WIND |  | LNCRK_G83 | SHACKELFORD | WIND | WEST | 2006 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
NOTREES WIND 1 |  | NWF_NWF1 | WINKLER/ECTOR | WIND | WEST | 2009 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6
NOTREES WIND 2 |  | NWF_NWF2 | WINKLER/ECTOR | WIND | WEST | 2009 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OCOTILLO WIND FARM |  | OWF_OWF | HOWARD | WIND | WEST | 2008 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8
PANTHER CREEK 1 |  | PC_NORTH_PANTHER1 | HOWARD | WIND | WEST | 2008 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5
PANTHER CREEK 2 |  | PC_SOUTH_PANTHER2 | HOWARD | WIND | WEST | 2008 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5
PANTHER CREEK 3 |  | PC_SOUTH_PANTHER3 | HOWARD | WIND | WEST | 2009 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5
PAPALOTE CREEK WIND |  | COTTON_PAP2 | SAN PATRICIO | WIND | SOUTH | 2010 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1
PAPALOTE CREEK WIND FARM |  | PAP1_PAP1 | SAN PATRICIO | WIND | SOUTH | 2009 | 179.85 | 179.85 | 179.85 | 179.85 | 179.85 | 179.85 | 179.85 | 179.85 | 179.85 | 179.85
PECOS WIND (WOODWARD 1) |  | WOODWRD1_WOODWRD1 | PECOS | WIND | WEST | 2001 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5
PECOS WIND (WOODWARD 2) |  | WOODWRD2_WOODWRD2 | PECOS | WIND | WEST | 2001 | 77.22 | 77.22 | 77.22 | 77.22 | 77.22 | 77.22 | 77.22 | 77.22 | 77.22 | 77.22
PENASCAL WIND |  | PENA_UNIT1 | KENEDY | WIND | SOUTH | 2009 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8
PENASCAL WIND |  | PENA_UNIT2 | KENEDY | WIND | SOUTH | 2009 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
PENASCAL WIND |  | PENA3_UNIT3 | KENEDY | WIND | SOUTH | 2011 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8
POST OAK WIND 1 |  | LNCRK2_G871 | SHACKELFORD | WIND | WEST | 2007 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
POST OAK WIND 2 |  | LNCRK2_G872 | SHACKELFORD | WIND | WEST | 2007 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
PYRON WIND FARM |  | PYR_PYRON1 | SCURRY/FISHER | WIND | WEST | 2008 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249
RED CANYON |  | RDCANYON_RDCNY1 | BORDEN | WIND | WEST | 2006 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
ROSCOE WIND FARM |  | TKWSW1_ROSCOE | NOLAN | WIND | WEST | 2008 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209
SAND BLUFF WIND FARM |  | MCDLD_SBW1 | GLASSCOCK | WIND | WEST | 2008 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
SENATE WIND PROJECT |  | SENATEWD_UNIT1 | JACK | WIND | WEST | 2012 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SHERBINO I |  | KEO_KEO_SM1 | PECOS | WIND | WEST | 2008 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SHERBINO 2 |  | KEO_SHRBINO2 | PECOS | WIND | WEST | 2011 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SILVER STAR |  | FLTCK_SSI | EASTLAND | WIND | NORTH | 2008 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SNYDER WIND FARM |  | ENAS_ENA1 | SCURRY | WIND | WEST | 2007 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
SOUTH TRENT WIND FARM |  | STWF_T1 | NOLAN/TAYLOR | WIND | WEST | 2008 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2
STANTON WIND ENERGY |  | SWEC_G1 | MARTIN | WIND | WEST | 2008 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
SWEETWATER WIND 1 |  | SWEETWND_WND1 | NOLAN | WIND | WEST | 2003 | 36.58 | 36.58 | 36.58 | 36.58 | 36.58 | 36.58 | 36.58 | 36.58 | 36.58 | 36.58
SWEETWATER WIND 2 |  | SWEETWN2_WND24 | NOLAN | WIND | WEST | 2006 | 15.87 | 15.87 | 15.87 | 15.87 | 15.87 | 15.87 | 15.87 | 15.87 | 15.87 | 15.87
SWEETWATER WIND 3 |  | SWEETWN2_WND2 | NOLAN | WIND | WEST | 2004 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5
SWEETWATER WIND 4 |  | SWEETWN3_WND3A | NOLAN | WIND | WEST | 2011 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5
SWEETWATER WIND 4 |  | SWEETWN3_WND3B | NOLAN | WIND | WEST | 2011 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5
SWEETWATER WIND 5 |  | SWEETWN4_WND5 | NOLAN | WIND | WEST | 2007 | 79.23 | 79.23 | 79.23 | 79.23 | 79.23 | 79.23 | 79.23 | 79.23 | 79.23 | 79.23
SWEETWATER WIND 6 |  | SWEETWN4_WND4B | NOLAN | WIND | WEST | 2007 | 103.65 | 103.65 | 103.65 | 103.65 | 103.65 | 103.65 | 103.65 | 103.65 | 103.65 | 103.65
SWEETWATER WIND 7 |  | SWEETWN4_WND4A | NOLAN | WIND | WEST | 2007 | 117.8 | 117.8 | 117.8 | 117.8 | 117.8 | 117.8 | 117.8 | 117.8 | 117.8 | 117.8
TEXAS BIG SPRING |  | SGMTN_SIGNALMT | HOWARD | WIND | WEST | 1999 | 34.32 | 34.32 | 34.32 | 34.32 | 34.32 | 34.32 | 34.32 | 34.32 | 34.32 | 34.32
TRENT WIND FARM |  | TRENT_TRENT | NOLAN | WIND | WEST | 2001 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
TRINITY HILLS |  | TRINITY_TH1_BUS1 | YOUNG | WIND | NORTH | 2012 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5 | 117.5
TRINITY HILLS |  | TRINITY_TH1_BUS2 | YOUNG | WIND | NORTH | 2012 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5
TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | NOLAN | WIND | WEST | 2008 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
TURKEY TRACK WIND ENERGY CENTER |  | TTWEC_G1 | NOLAN | WIND | WEST | 2008 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5
WEST TEXAS WIND ENERGY |  | SW_MESA_SW_MESA | UPTON/CROCKETT | WIND | WEST | 1999 | 74.2 | 74.2 | 74.2 | 74.2 | 74.2 | 74.2 | 74.2 | 74.2 | 74.2 | 74.2
WHIRLWIND ENERGY |  | WEC_WECG1 | FLOYD | WIND | NORTH | 2007 | 56.957 | 56.957 | 56.957 | 56.957 | 56.957 | 56.957 | 56.957 | 56.957 | 56.957 | 56.957
WHITETAIL WIND ENERGY PROJECT |  | EXGNWTL_WIND_1 | WEBB/DUVAL | WIND | SOUTH | 2012 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
WKN MOZART |  | MOZART_WIND_1 | KENT/STONEWALL | WIND | WEST | 2012 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
WOLFE RIDGE |  | WHTTAIL_WR1 | COOKE | WIND | NORTH | 2008 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5
Wind Capacity Total | [6 empty] | 11065.777 | 11065.777 | 11065.777 | 11065.777 | 11065.777 | 11065.777 | 11065.777 | 11065.777 | 11065.777 | 11065.777
Wind Capacity Total (Non-Coastal) | [6 empty] | 9382.727 | 9382.727 | 9382.727 | 9382.727 | 9382.727 | 9382.727 | 9382.727 | 9382.727 | 9382.727 | 9382.727
Wind Capacity Total (Coastal) | [6 empty] | 1683.05 | 1683.05 | 1683.05 | 1683.05 | 1683.05 | 1683.05 | 1683.05 | 1683.05 | 1683.05 | 1683.05
Wind Capacity (Coastal County) |  |  | SAN PATRICIO |  | SOUTH |  | 379.95 | 379.95 | 379.95 | 379.95 | 379.95 | 379.95 | 379.95 | 379.95 | 379.95 | 379.95
Wind Capacity (Coastal County) |  |  | NUECES |  | SOUTH |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
Wind Capacity (Coastal County) |  |  | KLEBERG |  | SOUTH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind Capacity (Coastal County) |  |  | KENEDY |  | SOUTH |  | 686.4 | 686.4 | 686.4 | 686.4 | 686.4 | 686.4 | 686.4 | 686.4 | 686.4 | 686.4
Wind Capacity (Coastal County) |  |  | WILLACY |  | SOUTH |  | 607.7 | 607.7 | 607.7 | 607.7 | 607.7 | 607.7 | 607.7 | 607.7 | 607.7 | 607.7
Wind Capacity (Coastal County) |  |  | CAMERON |  | SOUTH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
New Resources with Signed IA and Air Permit
PANDA SHERMAN CTG1 | 10INR0021 | PANDA_S_SHER1CT1 | GRAYSON | GAS | NORTH | 2014 | 220.05 | 220.05 | 220.05 | 220.05 | 220.05 | 220.05 | 220.05 | 220.05 | 220.05 | 220.05
PANDA SHERMAN CTG2 | 10INR0021 | PANDA_S_SHER1CT2 | GRAYSON | GAS | NORTH | 2014 | 220.05 | 220.05 | 220.05 | 220.05 | 220.05 | 220.05 | 220.05 | 220.05 | 220.05 | 220.05
PANDA SHERMAN STG | 10INR0021 | PANDA_S_SHER1ST1 | GRAYSON | GAS | NORTH | 2014 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6
PANDA TEMPLE CTG1 | 10INR0020a | PANDA_T1_TMPL1CT1 | BELL | GAS | NORTH | 2014 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5
PANDA TEMPLE CTG2 | 10INR0020a | PANDA_T1_TMPL1CT2 | BELL | GAS | NORTH | 2014 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5
PANDA TEMPLE STG | 10INR0020a | PANDA_T1_TMPL1ST1 | BELL | GAS | NORTH | 2014 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6
DEER PARK ENERGY CENTER | 14INR0015 | DDPEC_GT6 | HARRIS | GAS | HOUSTON | 2014 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190
FERGUSON REPLACEMENT CTG1 | 13INR0021 | FERGCC_FERGGT1 | LLANO | GAS | SOUTH | 2014 | 186.1 | 186.1 | 186.1 | 186.1 | 186.1 | 186.1 | 186.1 | 186.1 | 186.1 | 186.1
FERGUSON REPLACEMENT CTG2 | 13INR0021 | FERGCC_FERGGT2 | LLANO | GAS | SOUTH | 2014 | 186.1 | 186.1 | 186.1 | 186.1 | 186.1 | 186.1 | 186.1 | 186.1 | 186.1 | 186.1
FERGUSON REPLACEMENT STG | 13INR0021 | FERGCC_FERGST1 | LLANO | GAS | SOUTH | 2014 | 194.9 | 194.9 | 194.9 | 194.9 | 194.9 | 194.9 | 194.9 | 194.9 | 194.9 | 194.9
TEXAS CLEAN ENERGY PROJECT | 13INR0023 |  | ECTOR | COAL | WEST | 2018 | 0 | 0 | 0 | 0 | 240 | 240 | 240 | 240 | 240 | 240
PANDA TEMPLE II | 10INR0020b |  | BELL | GAS | NORTH | 2015 | 0 | 790 | 790 | 790 | 790 | 790 | 790 | 790 | 790 | 790
PONDERA KING POWER PROJECT | 10INR0022 |  | HARRIS | GAS | HOUSTON | 2018 | 0 | 0 | 0 | 0 | 1628.97 | 1628.97 | 1628.97 | 1628.97 | 1628.97 | 1628.97
RENTECH PROJECT | 13INR0040 |  | HARRIS | GAS | HOUSTON | 2014 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
FORNEY POWER UPGRADE GT11-13 | 14INR0059-A |  | KAUFMAN | GAS | NORTH | 2014 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
FORNEY POWER UPGRADE GT21-23 | 14INR0059-B |  | KAUFMAN | GAS | NORTH | 2015 | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
WHITE CAMP SOLAR | 11INR0094 | WCSOLAR1_100PV | KENT | SOLAR | WEST | 2014 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
MUSTANG SOLAR PROJECT | 13INR0031 |  | TRAVIS | SOLAR | SOUTH | 2015 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
OCI ALAMO 4 | 14INR0024 |  | KINNEY | SOLAR | SOUTH | 2014 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
PECOS BARILLA SOLAR | 12INR0059 | HOVEY_UNIT1 | PECOS | SOLAR | WEST | 2014 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
New Capacity Total (Not Wind) | [6 empty] | 2501.4 | 3308.4 | 3338.4 | 3338.4 | 5207.37 | 5207.37 | 5207.37 | 5207.37 | 5207.37 | 5207.37
New Wind Resources
STEPHENS RANCH WIND ENERGY | 12INR0034 |  | BORDEN | WIND | WEST | 2014 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378 | 378
GOLDTHWAITE WIND 1 | 11INR0013 | GWEC_GWEC_G1 | MILLS | WIND | NORTH | 2014 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6
SPINNING SPUR WIND TWO | 13INR0048 | SSPURTWO_WIND_1 | OLDHAM | WIND | PANHANDLE | 2014 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161
MARIAH WIND a | 13INR0010a |  | PARMER | WIND | PANHANDLE | 2014 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232
PANHANDLE WIND | 14INR0030a_2 |  | CARSON | WIND | PANHANDLE | 2014 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218
PANHANDLE WIND 2 | 14INR0030b |  | CARSON | WIND | PANHANDLE | 2015 | 0 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182
MIAMI WIND 1a | 14INR0012a | MIAM1_G1, G2 | GRAY | WIND | PANHANDLE | 2014 | 288.9 | 288.9 | 288.9 | 288.9 | 288.9 | 288.9 | 288.9 | 288.9 | 288.9 | 288.9
MOORE WIND 1 | 11INR0050 |  | CROSBY | WIND | WEST | 2014 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149
MARIAH WIND b | 13INR0010b |  | PARMER | WIND | PANHANDLE | 2015 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
MIDWAY FARMS WIND | 11INR0054 |  | SAN PATRICIO | WIND | SOUTH | 2015 | 0 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161
LONGHORN ENERGY CENTER | 14INR0023 |  | BRISCOE | WIND | WEST | 2014 | 361 | 361 | 361 | 361 | 361 | 361 | 361 | 361 | 361 | 361
CONWAY WINDFARM | 13INR0005 |  | CARSON | WIND | PANHANDLE | 2014 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
SOUTH CLAY WINDFARM | 11INR0079a |  | CLAY | WIND | WEST | 2014 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
PENASCAL WIND FARM 3 | 06INR0022c |  | KENEDY | WIND | SOUTH | 2014 | 0 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202
MARIAH WIND c | 13INR0010c |  | PARMER | WIND | PANHANDLE | 2016 | 0 | 0 | 0 | 168 | 168 | 168 | 168 | 168 | 168 | 168
MESQUITE CREEK | 09INR0051 |  | BORDEN | WIND | WEST | 2015 | 0 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249
GUNSIGHT MOUNTAIN | 08INR0018 |  | HOWARD | WIND | WEST | 2015 | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
BRISCOE WIND FARM | 14INR0072 |  | BRISCOE | WIND | WEST | 2015 | 0 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
CAMERON COUNTY WIND | 11INR0057 |  | CAMERON | WIND | SOUTH | 2015 | 0 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
COMANCHE RUN WIND | 12INR0029 |  | SWISHER | WIND | PANHANDLE | 2016 | 0 | 0 | 0 | 500 | 500 | 500 | 500 | 500 | 500 | 500
CPV RATTLESNAKE DEN PH 1 | 13INR0020a |  | GLASSCOCK | WIND | WEST | 2015 | 0 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201
CPV RATTLESNAKE DEN PH 2 | 13INR0020b |  | GLASSCOCK | WIND | WEST | 2016 | 0 | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
GREEN PASTURES WIND | 12INR0070 |  | KNOX | WIND | WEST | 2015 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
HEREFORD WIND a | 13INR0059a |  | CASTRO | WIND | PANHANDLE | 2014 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
JUMBO ROAD WIND b | 13INR0059b |  | CASTRO | WIND | PANHANDLE | 2015 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
KEECHI WIND 138 KV JOPLIN | 14INR0049_2 |  | JACK | WIND | NORTH | 2014 | 0 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
LOGANS GAP WIND I | 13INR0050 |  | COMANCHE | WIND | NORTH | 2015 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
LOS VIENTOS III | 13INR0052 |  | STARR | WIND | SOUTH | 2014 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
MIAMI WIND 1b | 14INR0012b |  | GRAY | WIND | PANHANDLE | 2015 | 0 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111
PAMPA WIND PROJECT | 12INR0018 |  | GRAY | WIND | PANHANDLE | 2017 | 0 | 0 | 0 | 500 | 500 | 500 | 500 | 500 | 500 | 500
PATRIOT (PETRONILLA) WIND | 11INR0062 |  | NUECES | WIND | SOUTH | 2015 | 0 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
ROUTE66 WIND | 14INR0032a |  | RANDALL | WIND | PANHANDLE | 2014 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SENDERO WIND ENERGY PROJECT | 12INR0068 |  | JIM HOGG | WIND | SOUTH | 2015 | 0 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
SOUTH PLAINS WIND I | 14INR0025a |  | FLOYD | WIND | WEST | 2015 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
SOUTH PLAINS WIND II | 14INR0025b |  | FLOYD | WIND | WEST | 2015 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
SPINNING SPUR WIND THREE | 14INR0053 |  | OLDHAM | WIND | PANHANDLE | 2014 | 0 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194
WINDTHORST 2 | 13INR0057 |  | ARCHER | WIND | NORTH | 2014 | 0 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
New Wind Capacity Total | [6 empty] | 2886.5 | 6594.5 | 7244.5 | 8412.5 | 8412.5 | 8412.5 | 8412.5 | 8412.5 | 8412.5 | 8412.5
New Wind Capacity Total (Non-Coastal) | [6 empty] | 2886.5 | 5888.5 | 6538.5 | 7706.5 | 7706.5 | 7706.5 | 7706.5 | 7706.5 | 7706.5 | 7706.5
New Wind Capacity Total (Coastal) | [6 empty] | 0 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706
New Wind Capacity (Coastal County) |  |  | SAN PATRICIO |  | SOUTH |  | 0 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161
New Wind Capacity (Coastal County) |  |  | NUECES |  | SOUTH |  | 0 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
New Wind Capacity (Coastal County) |  |  | KLEBERG |  | SOUTH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
New Wind Capacity (Coastal County) |  |  | KENEDY |  | SOUTH |  | 0 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 202
New Wind Capacity (Coastal County) |  |  | WILLACY |  | SOUTH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
New Wind Capacity (Coastal County) |  |  | CAMERON |  | SOUTH |  | 0 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
Switchable Capacity Unavailable to ERCOT |  |  |  | GAS |  |  | -330 | -330 | -330 | -330 | -330 | -330 | -330 | 0 | 0 | 0
Available Mothball Capacity based on Owner's Return Probability |  |  |  | COAL |  |  | 0 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58
Retiring Capacity
AES DEEPWATER |  | APD_APD_PS1 | HARRIS | STORAGE | HOUSTON | 2010 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
Total Retiring Units | [6 empty] | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
Mothballed Capacity
APPLIED ENERGY |  | APD_APD_G1 | HARRIS | OTHER | HOUSTON | 1986 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140
ATKINS |  | ATKINS_ATKINSG3 | BRAZOS | GAS | NORTH | 1954 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
ATKINS |  | ATKINS_ATKINSG4 | BRAZOS | GAS | NORTH | 1958 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
ATKINS |  | ATKINS_ATKINSG5 | BRAZOS | GAS | NORTH | 1965 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
ATKINS |  | ATKINS_ATKINSG6 | BRAZOS | GAS | NORTH | 1969 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
GREENS BAYOU |  | GBY_GBYGT82 | HARRIS | GAS | HOUSTON | 1976 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58
NORTH TEXAS |  | NTX_NTX_1 | PARKER | GAS | NORTH | 1958 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
NORTH TEXAS |  | NTX_NTX_2 | PARKER | GAS | NORTH | 1958 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
NORTH TEXAS |  | NTX_NTX_3 | PARKER | GAS | NORTH | 1963 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
PERMIAN BASIN SES |  | PBSES_UNIT6 | WARD | GAS | WEST | 1973 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530
SILAS RAY |  | SILASRAY_SILAS_5 | CAMERON | GAS | SOUTH | 1953 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
VALLEY SES |  | VLSES_UNIT1 | FANNIN | GAS | NORTH | 1962 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174
VALLEY SES |  | VLSES_UNIT2 | FANNIN | GAS | NORTH | 1967 | 520 | 520 | 520 | 520 | 520 | 520 | 520 | 520 | 520 | 520
VALLEY SES |  | VLSES_UNIT3 | FANNIN | GAS | NORTH | 1971 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375
J T DEELY 1 |  | CALAVERS_JTD1 | BEXAR | COAL | SOUTH | 1977 | 0 | 0 | 0 | 0 | 0 | 430 | 430 | 430 | 430 | 430
J T DEELY 2 |  | CALAVERS_JTD2 | BEXAR | COAL | SOUTH | 1978 | 0 | 0 | 0 | 0 | 0 | 420 | 420 | 420 | 420 | 420
SR BERTRON |  | SRB_SRBGT_2 | HARRIS | GAS | HOUSTON | 1967 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
SR BERTRON |  | SRB_SRB_G1 | HARRIS | GAS | HOUSTON | 1958 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118
SR BERTRON |  | SRB_SRB_G2 | HARRIS | GAS | HOUSTON | 1956 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174
SR BERTRON |  | SRB_SRB_G3 | HARRIS | GAS | HOUSTON | 1959 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211
SR BERTRON |  | SRB_SRB_G4 | HARRIS | GAS | HOUSTON | 1960 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211
Total Mothballed Capacity | [6 empty] | 2718 | 2718 | 2718 | 2718 | 2718 | 3568 | 3568 | 3568 | 3568 | 3568
Seasonal Mothballed Capacity
MARTIN LAKE 3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820
MONTICELLO 1 |  | MNSES_UNIT1 | TITUS | COAL | NORTH | 1974 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580
MONTICELLO 2 |  | MNSES_UNIT2 | TITUS | COAL | NORTH | 1975 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580
Total Seasonal Mothballed Capacity | [6 empty] | 1980 | 1980 | 1980 | 1980 | 1980 | 1980 | 1980 | 1980 | 1980 | 1980
Excluded Resources, per notification from developer
COBISA-GREENVILLE | 06INR0006 |  | HUNT | GAS |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A

## SummerFuelTypes
Summer Fuel Types - ERCOT
Fuel type is based on the primary fuel. Capacities of the wind units are included at 8.7%. Hydro and DC Tie Imports are included based on the three-year average historical maximum capability for each year's 20 peak load hours. The amounts available for the grid according to information from the owners of the private network (self-serve) units and the distributed generation units that have registered with ERCOT are included. DC Tie imports are catetorized as Other and mothballed capacity is excluded.
In MW
Fuel Type | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023
Biomass | 235.349 | 235.349 | 235.349 | 235.349 | 235.349 | 235.349 | 235.349 | 235.349 | 235.349 | 235.349
Coal | 19882 | 19940 | 19213 | 19213 | 19213 | 18613 | 18613 | 18613 | 18613 | 18613
Gas | 46292.337 | 48445.337 | 49188.337 | 49188.337 | 50656.937 | 50656.937 | 50656.937 | 50956.937 | 50956.937 | 50956.937
Nuclear | 5150 | 5150 | 5150 | 5150 | 5150 | 5150 | 5150 | 5150 | 5150 | 5150
Other | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3
Hydro | 446.2 | 446.2 | 446.2 | 446.2 | 446.2 | 446.2 | 446.2 | 446.2 | 446.2 | 446.2
Wind | 989.6578 | 1427.4331 | 1592.9071 | 1694.5231 | 1694.5231 | 1694.5231 | 1694.5231 | 1694.5231 | 1694.5231 | 1694.5231
Solar | 252.943 | 290.543 | 320.543 | 320.543 | 320.543 | 320.543 | 320.543 | 320.543 | 320.543 | 320.543
Storage | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7
Total | 73925.4868 | 76611.8621 | 76823.3361 | 76924.9521 | 78393.5521 | 77793.5521 | 77793.5521 | 78093.5521 | 78093.5521 | 78093.5521
In Percentages
Fuel Type | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023
Biomass | 0.3184% | 0.3072% | 0.3064% | 0.3059% | 0.3002% | 0.3025% | 0.3025% | 0.3014% | 0.3014% | 0.3014%
Coal | 26.89% | 26.03% | 25.01% | 24.98% | 24.51% | 23.93% | 23.93% | 23.83% | 23.83% | 23.83%
Natural Gas | 62.62% | 63.23% | 64.03% | 63.94% | 64.62% | 65.12% | 65.12% | 65.25% | 65.25% | 65.25%
Nuclear | 6.966% | 6.722% | 6.704% | 6.695% | 6.569% | 6.62% | 6.62% | 6.595% | 6.595% | 6.595%
Other | 0.8702% | 0.8397% | 0.8374% | 0.8363% | 0.8206% | 0.8269% | 0.8269% | 0.8238% | 0.8238% | 0.8238%
Hydro | 0.6036% | 0.5824% | 0.5808% | 0.58% | 0.5692% | 0.5736% | 0.5736% | 0.5714% | 0.5714% | 0.5714%
Wind | 1.339% | 1.863% | 2.073% | 2.203% | 2.162% | 2.178% | 2.178% | 2.17% | 2.17% | 2.17%
Solar | 0.3422% | 0.3792% | 0.4172% | 0.4167% | 0.4089% | 0.412% | 0.412% | 0.4105% | 0.4105% | 0.4105%
Storage | 0.04559% | 0.04399% | 0.04387% | 0.04381% | 0.04299% | 0.04332% | 0.04332% | 0.04315% | 0.04315% | 0.04315%

## WinterFuelTypes
Winter Fuel Types - ERCOT
Fuel type is based on the primary fuel. Capacities of the wind units are included at 8.7%. Hydro and DC Tie Imports are included based on the three-year average historical maximum capability for each year's 20 peak load hours. The amounts available for the grid according to information from the owners of the private network (self-serve) units and the distributed generation units that have registered with ERCOT are included. DC Tie imports are categorized as Other and mothballed capacity is excluded.
In MW
Fuel Type | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24
Biomass | 235.349 | 235.349 | 235.349 | 235.349 | 235.349 | 235.349 | 235.349 | 235.349 | 235.349 | 235.349
Coal | 17357 | 17415 | 17415 | 17415 | 17655 | 16805 | 16805 | 16805 | 16805 | 16805
Gas | 50801.5571 | 51608.5571 | 51608.5571 | 51608.5571 | 53237.527 | 53237.527 | 53237.527 | 53567.527 | 53567.527 | 53567.527
Nuclear | 5210 | 5210 | 5210 | 5210 | 5210 | 5210 | 5210 | 5210 | 5210 | 5210
Other | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3 | 643.3
Hydro | 446.2 | 446.2 | 446.2 | 446.2 | 446.2 | 446.2 | 446.2 | 446.2 | 446.2 | 446.2
Wind | 1213.8481 | 1536.4441 | 1592.9941 | 1694.6101 | 1694.6101 | 1694.6101 | 1694.6101 | 1694.6101 | 1694.6101 | 1694.6101
Solar | 290.893 | 290.893 | 320.893 | 320.893 | 320.893 | 320.893 | 320.893 | 320.893 | 320.893 | 320.893
Storage | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7
Total | 76231.8472 | 77419.4432 | 77505.9932 | 77607.6092 | 79476.5791 | 78626.5791 | 78626.5791 | 78956.5791 | 78956.5791 | 78956.5791
In Percentages
Fuel Type | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24
Biomass | 0.3087% | 0.304% | 0.3037% | 0.3033% | 0.2961% | 0.2993% | 0.2993% | 0.2981% | 0.2981% | 0.2981%
Coal | 22.77% | 22.49% | 22.47% | 22.44% | 22.21% | 21.37% | 21.37% | 21.28% | 21.28% | 21.28%
Gas | 66.64% | 66.66% | 66.59% | 66.5% | 66.99% | 67.71% | 67.71% | 67.84% | 67.84% | 67.84%
Nuclear | 6.834% | 6.73% | 6.722% | 6.713% | 6.555% | 6.626% | 6.626% | 6.599% | 6.599% | 6.599%
Other | 0.8439% | 0.8309% | 0.83% | 0.8289% | 0.8094% | 0.8182% | 0.8182% | 0.8148% | 0.8148% | 0.8148%
Hydro | 0.5853% | 0.5763% | 0.5757% | 0.5749% | 0.5614% | 0.5675% | 0.5675% | 0.5651% | 0.5651% | 0.5651%
Wind | 1.592% | 1.985% | 2.055% | 2.184% | 2.132% | 2.155% | 2.155% | 2.146% | 2.146% | 2.146%
Solar | 0.3816% | 0.3757% | 0.414% | 0.4135% | 0.4038% | 0.4081% | 0.4081% | 0.4064% | 0.4064% | 0.4064%
Storage | 0.04421% | 0.04353% | 0.04348% | 0.04342% | 0.0424% | 0.04286% | 0.04286% | 0.04268% | 0.04268% | 0.04268%