## Slide 1: PDCWG Report to ROS
David Kee Chair
CPS Energy
Sydney Niemeyer Vice Chair
NRG Energy

## Slide 2: January Meeting
Leadership nomination
Review of early release of HASL to SCED
NPRR576 review
SCR773 performance metrics review
Frequency Event Review

## Slide 3: PDCWG Leadership – 2014
Chair – Don Blackburn
Vice Chair – Sydney Niemeyer

## Slide 4: Early Release of HASL to SCED
Q: When should HASL be released (manually deploy RRS) such that 2300MW of frequency responsive RRS always be held in reserve?
A:Would release too early if at 3300 PRC except for one time in the last year.
  PDCWG agrees with this point
When Non Spin is deployed (PRC at 2500MW) this is a point where HASL can be released for portion of RRS(between “X”MW and 500 MW transferred from Non Spinning based on ramp limitations)
  PDCWG has no objection to this proposal. Concern is how to do it appropriately.
  Issue that some RRS may have already been deployed.
  Issue with knowing what capacity is frequency responsive (20% frequency responsive vs 24% base plus 4% nonfrequency responsive)
When Out of Regulation Up and no SCED Up room
  between “X”MW and 500 MW transferred from Non Spinning based on ramp limitations
Below 2300 Spinning.
  between “X”MW and 500 MW transferred from Non Spinning based on ramp limitations
When below 3000 PRC and forward indications suggest going into EEA
  between “X”MW and 500 MW transferred from Non Spinning based on ramp limitations

## Slide 5: PDCWG Considerations/Suggestions for further analysis
Change how ERCOT counts startup and shutdown in Spinning and PRC calculations and evaluate the results during the extreme events (1/6/14)
Evaluate Ramp Rates
  Account for ramp rates in the Spinning and PRC calculations and evaluate extreme events
  Research any correlation between HDL and Ramp Rates
  Understand Emergency Ramp Rate behavior
Evaluate telemetry latency
Responsive Reserve deployment timing and functionality
  Improve time from energy need to energy delivery
Consider the load resources carrying RRS
  Ratio changes when 500MW is only released from generators
Consider Real Time Reserve Forecast based on load and gen forecast
Consider how the various cap limits effect constraints and the stranded energy behind the constraints

## Slide 6: NPRR 576
PDCWG doesn’t support this NPRR as written.
Issues:
  Operational benefits from Online NonSpinning Reserve
  Possibly update the reserve accounting by ERCOT.
  Take Online NonSpin out of PRC calculations.

## Slide 7
Questions?