## Summary
Preliminary
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Summer 2014
Released March 5, 2014
SUMMARY
ERCOT expects to start this summer with tight reserves. However, by late summer, four new combined-cycle gas-fired power plants, with a combined summer capacity rating of 2,112 megawatts (MW), are expected to begin commercial operations. Completion of these projects  Ferguson, Panda Sherman, Panda Temple I and Deer Park Energy Center  will increase the overall planning reserve margin and significantly reduce the likelihood of scarcity conditions by late summer. The commercial operations date for the Deer Park plant is currently July 1, 2014, with both Panda plants and the new Ferguson unit expected to begin commercial operations by August 1, 2014.
If an extreme system peak occurs prior to completion of the new units, those conditions could result in an Energy Emergency Alert (EEA), with corresponding public appeals for conservation. Depending on the severity of the situation and the amount of generation available during periods of highest demand, ERCOT could take other progressive steps necessary to protect overall system integrity.
Wind generation resources continue to count at 8.7 percent of nameplate capacity in this assessment. Capacity ratings for other generation resources are lower in the summer due to the effects of higher ambient temperatures.
ERCOT continues to monitor the persistent drought conditions throughout Texas. While reservoir levels are not expected to drop below power plant physical intake limits during summer 2014, ERCOT continues to assess potential risks to generation operations.

## Scenarios
Preliminary
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Summer 2014
Release Date: March 5, 2014
Forecasted Resources and Demand
|  | Installed Capacity, MW | 64993.329 | Based on current Seasonal Maximum Sustainable Limits reported through the unit registration process
|  | Planned Units (not wind) with Signed IA and Air Permit, MW | 130 | Based on in-service dates provided by developers of generation resources
|  | Capacity from Private Networks, MW | 4655 | Based on actual historical net PUN output
|  | Switchable Units, MW | 2977 | Installed capacity of units that can switch to other Regions
|  | less Switchable Units Unavailable to ERCOT, MW | -300 | Based on survey responses of Switchable Unit owners
|  | RMR Units to be under Contract, MW | 0
|  | Effective Load-Carrying Capability (ELCC) of Wind Generation, MW | 962.7226 | Based on 8.7% of installed capacity (Effective Load Carrying Capability) of wind per ERCOT Nodal Protocols Section 3.2.6.2.2
|  | ELCC of Planned Wind Units with Signed IA, MW | 14.007 | Based on in-service dates provided by developers of generation resources
|  | Non-Synchronous Ties, MW | 643 | Average maximum capability of the top 20 hours for the past three years
a | Total Resources, MW |  | 74075.0586
b | Peak Demand, MW |  | 68096 | Summer peak forecast based on normal weather conditions for 2002 - 2013
c | Reserve Capacity (a - b), MW |  | 5979.0586
Range of Potential Risks
|  |  | Summer Peak Forecast Based on Normal Weather Conditions for 2002 – 2013 (August) | Extreme Load/Typical Gen Outages | Extreme Load/Extreme Generation Outages
|  | Seasonal Load Adjustment |  | 2313 | 2313
|  | Typical Maintenance Outages | 356 | 356 | 356 |  | Based on historical (August 2010 to February 18, 2014) average of planned outages for June through September weekdays
|  | Typical Forced Outages | 2574 | 2574 | 2574 |  | Based on historical (August 2010 to February 18, 2014) average of forced outages for June through September weekdays
|  | 90th Percentile Forced Outages |  | 0 | 2792
d | Total Uses of Reserve Capacity |  | 2930 | 5243 | 8035
e | Capacity Available for Operating Reserves (c-d), MW |  | 3049.0586 | 736.0586 | -2055.9414
Less than 2,300 MW indicates risk of EEA1
f | Capacity (non-wind) scheduled to be operational by August 1 |  | 2112 | 2112 | 2112
g | Capacity Available for Operating Reserves (e+f), MW |  | 5161.0586 | 2848.0586 | 56.0586 | 0

## Inputs for Sensitivities
Preliminary
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Summer 2014
Release Date: March 5, 2014
Scenario Inputs
| Forecasted Peak Load for Summer 2014 | 68096 | Summer peak forecast based on normal weather conditions for 2002 – 2013
| Load Adjustment for July - August Peak | 2313 | Summer extreme forecast using 2011 weather (70,409 MW)
| Typical Maintenance Outages | 356 | Based on historical (August 2010 to February 18, 2014) average of planned outages for June through September weekdays
| Typical Forced Outages | 2574 | Based on historical (August 2010 to February 18, 2014) average of forced outages for June through September weekdays
| 90th Percentile Forced Outages | 2792

## Unit Listing
Unit Code | Plant Name | Primary Energy Source | Spring Capacity (MW) | Status
AZ_AZ_G1 | AIRPRO | NG | 38 | Existing
AZ_AZ_G2 | AIRPRO | NG | 38 | Existing
AZ_AZ_G3 | AIRPRO | NG | 38 | Existing | Key to Abbreviations
AZ_AZ_G4 | AIRPRO | NG | 38 | Existing | BIO | Biomass
HB_DG1 | ATASCOCITA | LFG | 10 | Nonmod | BIT | Bituminous Coal
ATKINS_ATKINSG7 | ATKINS | NG | 20 | Existing | LFG | Land-fill Gas
DG_SPRIN_4UNITS | AUSTIN LANDFILL GAS | UNK | 6.4 | Nonmod | LIG | Lignite Coal
B_DAVIS_B_DAVIG1 | BARNEY DAVIS | NG | 335 | Existing | MTE | Methanol
B_DAVIS_B_DAVIG2 | BARNEY DAVIS | NG | 319 | Existing | MTH | Methane
B_DAVIS_B_DAVIG3 | BARNEY DAVIS | NG | 157 | Existing | NG | Natural Gas
B_DAVIS_B_DAVIG4 | BARNEY DAVIS | NG | 157 | Existing | NUC | Nuclear
BASTEN_GTG1100 | BASTROP ENERGY CENTER | NG | 150 | Existing | OG | Other Gas
BASTEN_GTG2100 | BASTROP ENERGY CENTER | NG | 150 | Existing | OTH | Other
BASTEN_ST0100 | BASTROP ENERGY CENTER | WH | 233 | Existing | PC | Pulverized Coal
TRN_DG1 | BAYTOWN | MTH | 3.872 | Nonmod | SUB | Sub-bituminous Coal
BBSES_UNIT1 | BIG BROWN SES | LIG | 600 | Existing | SUN | Sun (Solar Resource)
BBSES_UNIT2 | BIG BROWN SES | LIG | 595 | Existing | UNK | Unknown
DG_BIOE_2UNITS | BIO ENERGY PARTNERS | NG | 6.2 | Nonmod | WAT | Water (Hydro Resource)
DG_BROOK_1UNIT | BLUE WING SOLAR 1 | SUN | 7.56 | Nonmod | WDS | Wood Biomass
DG_ELMEN_1UNIT | BLUE WING SOLAR 2 | SUN | 7.3 | Nonmod | WH | Waste Heat
LB_DG1 | BLUEBONNET | LFG | 3.872 | Nonmod | WND | Wind
BOSQUESW_BSQSU_1 | BOSQUE SWITCH | NG | 143.2 | Existing | NA | Unknown
BOSQUESW_BSQSU_2 | BOSQUE SWITCH | NG | 143.2 | Existing
BOSQUESW_BSQSU_3 | BOSQUE SWITCH | NG | 150.2 | Existing
BOSQUESW_BSQSU_4 | BOSQUE SWITCH | WH | 81.4 | Existing
BOSQUESW_BSQSU_5 | BOSQUE SWITCH | WH | 190.5 | Existing
BVE_UNIT1 | BRAZOS VALLEY ENERGY LP | NG | 166 | Existing
BVE_UNIT2 | BRAZOS VALLEY ENERGY LP | NG | 166 | Existing
BVE_UNIT3 | BRAZOS VALLEY ENERGY LP | NG | 270 | Existing
ACACIA_UNIT_1 | ACACIA SOLAR | SUN | 9.99 | Existing
FLCNS_UNIT1 | CAL ENERGY | NG | 75 | Existing
FLCNS_UNIT2 | CAL ENERGY | NG | 75 | Existing
FLCNS_UNIT3 | CAL ENERGY | NG | 70 | Existing
CALAVERS_OWS1 | CALAVERAS | NG | 420 | Existing
CALAVERS_OWS2 | CALAVERAS | NG | 420 | Existing
CALAVERS_JKS1 | CALAVERAS | SUB | 555 | Existing
CALAVERS_JKS2 | CALAVERAS | SUB | 775 | Existing
CALAVERS_JTD1 | CALAVERAS | SUB | 420 | Existing
CALAVERS_JTD2 | CALAVERAS | SUB | 420 | Existing
CBY4_CT41 | CEDAR BAYOU 4 | NG | 163 | Existing
CBY4_CT42 | CEDAR BAYOU 4 | NG | 163 | Existing
CBY4_ST04 | CEDAR BAYOU 4 | NG | 178 | Existing
CBY_CBY_G1 | CEDAR BAYOU PLANT | NG | 745 | Existing
CBY_CBY_G2 | CEDAR BAYOU PLANT | NG | 749 | Existing
CVC_CVC_G1 | CHANNELVIEW COGEN | NG | 155.4 | Existing
CVC_CVC_G2 | CHANNELVIEW COGEN | NG | 165.1 | Existing
CVC_CVC_G3 | CHANNELVIEW COGEN | NG | 163.9 | Existing
CVC_CVC_G5 | CHANNELVIEW COGEN | NG | 134.2 | Existing
AV_DG1 | COASTAL PLAINS RDF | LFG | 6.7 | Nonmod
COLETO_COLETOG1 | COLETO CREEK | SUB | 650 | Existing
CBEC_GT1 | COLORADO BEND ENERGY CENTER | NG | 76 | Existing
CBEC_GT2 | COLORADO BEND ENERGY CENTER | NG | 69 | Existing
CBEC_GT3 | COLORADO BEND ENERGY CENTER | NG | 72 | Existing
CBEC_GT4 | COLORADO BEND ENERGY CENTER | NG | 72 | Existing
CBEC_STG1 | COLORADO BEND ENERGY CENTER | NG | 103 | Existing
CBEC_STG2 | COLORADO BEND ENERGY CENTER | NG | 106 | Existing
CPSES_UNIT1 | COMANCHE PEAK SES | NUC | 1205 | Existing
CPSES_UNIT2 | COMANCHE PEAK SES | NUC | 1195 | Existing
DG_MEDIN_1UNIT | COVEL GARDENS LG POWER STATION | UNK | 9.6 | Nonmod
DANSBY_DANSBYG1 | DANSBY | NG | 110 | Existing
DANSBY_DANSBYG2 | DANSBY | NG | 48 | Existing
DANSBY_DANSBYG3 | DANSBY | NG | 48 | Existing
DECKER_DPG1 | DECKER POWER PLANT | NG | 315 | Existing
DECKER_DPG2 | DECKER POWER PLANT | NG | 420 | Existing
DECKER_DPGT_1 | DECKER POWER PLANT | NG | 48 | Existing
DECKER_DPGT_2 | DECKER POWER PLANT | NG | 48 | Existing
DECKER_DPGT_3 | DECKER POWER PLANT | NG | 48 | Existing
DECKER_DPGT_4 | DECKER POWER PLANT | NG | 48 | Existing
DCSES_CT10 | DECORDOVA SES CONSTELLATION | NG | 71 | Existing
DCSES_CT20 | DECORDOVA SES CONSTELLATION | NG | 70 | Existing
DCSES_CT30 | DECORDOVA SES CONSTELLATION | NG | 69 | Existing
DCSES_CT40 | DECORDOVA SES CONSTELLATION | NG | 68 | Existing
DDPEC_GT1 | DEER PARK ENERGY CENTER | NG | 181 | Existing
DDPEC_GT2 | DEER PARK ENERGY CENTER | NG | 193 | Existing
DDPEC_GT3 | DEER PARK ENERGY CENTER | NG | 181 | Existing
DDPEC_GT4 | DEER PARK ENERGY CENTER | NG | 193 | Existing
DDPEC_ST1 | DEER PARK ENERGY CENTER | WH | 290 | Existing
DG_BIO2_4UNITS | DFW GAS RECOVERY | LFG | 6.4 | Nonmod
DUKE_DUKE_GT1 | DUKE (NOW HIDALGO) | NG | 143 | Existing
DUKE_DUKE_GT2 | DUKE (NOW HIDALGO) | NG | 143 | Existing
DUKE_DUKE_ST1 | DUKE (NOW HIDALGO) | WH | 172 | Existing
FPPYD1_FPP_G1 | FAYETTE PLANT 1 & 2 | SUB | 604 | Existing
FPPYD1_FPP_G2 | FAYETTE PLANT 1 & 2 | SUB | 599 | Existing
FPPYD2_FPP_G3 | FAYETTE PLANT 3 | SUB | 441 | Existing
FRNYPP_GT11 | FORNEY | NG | 168.4 | Existing
FRNYPP_GT12 | FORNEY | NG | 168.4 | Existing
FRNYPP_GT13 | FORNEY | NG | 168.4 | Existing
FRNYPP_GT21 | FORNEY | NG | 168.4 | Existing
FRNYPP_GT22 | FORNEY | NG | 168.4 | Existing
FRNYPP_GT23 | FORNEY | NG | 168.4 | Existing
FRNYPP_ST10 | FORNEY | NG | 401.2 | Existing
FRNYPP_ST20 | FORNEY | NG | 401.2 | Existing
FREC_GT1 | Freestone Energy Center | NG | 151.56 | Existing
FREC_GT2 | Freestone Energy Center | NG | 151.56 | Existing
FREC_GT4 | Freestone Energy Center | NG | 151.69 | Existing
FREC_GT5 | Freestone Energy Center | NG | 151.69 | Existing
FREC_ST3 | Freestone Energy Center | WH | 176.23 | Existing
FREC_ST6 | Freestone Energy Center | WH | 174.47 | Existing
FRONTERA_FRONTEG1 | FRONTERA | NG | 165 | Existing
FRONTERA_FRONTEG2 | FRONTERA | NG | 165 | Existing
FRONTERA_FRONTEG3 | FRONTERA | WH | 180 | Existing
DG_RDLML_1UNIT | FW REGIONAL LFG GENERATION FACILITY | UNK | 1.6 | Nonmod
DG_LKWDT_2UNITS | GBRA | WAT | 4.8 | Nonmod
STEAM_ENGINE_1 | GEUS | NG | 8.439 | Existing
STEAM_ENGINE_2 | GEUS | NG | 8.439 | Existing
STEAM_ENGINE_3 | GEUS | NG | 8.439 | Existing
STEAM_STEAM_2 | GEUS | NG | 26 | Existing
STEAM_STEAM_3 | GEUS | NG | 41 | Existing
STEAM1A_STEAM_1 | GEUS | NG | 20 | Existing
GIBCRK_GIB_CRG1 | GIBBONS CREEK | SUB | 470 | Existing
GRSES_UNIT1 | GRAHAM SES | NG | 225 | Existing
GRSES_UNIT2 | GRAHAM SES | NG | 390 | Existing
GBY_GBY_5 | GREENS BAYOU | NG | 406 | Existing
GBY_GBYGT73 | GREENS BAYOU | NG | 46 | Existing
GBY_GBYGT74 | GREENS BAYOU | NG | 46 | Existing
GBY_GBYGT81 | GREENS BAYOU | NG | 46 | Existing
GBY_GBYGT83 | GREENS BAYOU | NG | 56 | Existing
GBY_GBYGT84 | GREENS BAYOU | NG | 58 | Existing
GUADG_GAS1 | GUADALUPE GEN | NG | 148 | Existing
GUADG_GAS2 | GUADALUPE GEN | NG | 148 | Existing
GUADG_GAS3 | GUADALUPE GEN | NG | 148 | Existing
GUADG_GAS4 | GUADALUPE GEN | NG | 148 | Existing
GUADG_STM5 | GUADALUPE GEN | NG | 197 | Existing
GUADG_STM6 | GUADALUPE GEN | NG | 197 | Existing
HLSES_UNIT3 | HANDLEY SES | NG | 395 | Existing
HLSES_UNIT4 | HANDLEY SES | NG | 435 | Existing
HLSES_UNIT5 | HANDLEY SES | NG | 435 | Existing
HAYSEN_HAYSENG1 | HAYS ENERGY | NG | 216 | Existing
HAYSEN_HAYSENG2 | HAYS ENERGY | NG | 216 | Existing
HAYSEN_HAYSENG3 | HAYS ENERGY | NG | 225 | Existing
HAYSEN_HAYSENG4 | HAYS ENERGY | NG | 225 | Existing
JACKCNTY_CT1 | JACK COUNTY PLANT | NG | 166 | Existing
JACKCNTY_CT2 | JACK COUNTY PLANT | NG | 165 | Existing
JCKCNTY2_CT3 | JACK COUNTY PLANT | NG | 166 | Existing
JCKCNTY2_CT4 | JACK COUNTY PLANT | NG | 165 | Existing
JACKCNTY_STG | JACK COUNTY PLANT | WH | 295 | Existing
JCKCNTY2_ST2 | JACK COUNTY PLANT | WH | 295 | Existing
DG_KMASB_1UNIT | KMAYBTO | OG | 0.125 | Nonmod
LH2SES_UNIT2 | LAKE HUBBARD 2 SES | NG | 515 | Existing
LHSES_UNIT1 | LAKE HUBBARD SES | NG | 392 | Existing
LPCCS_CT11 | LAMAR POWER PARTNERS | NG | 153.8 | Existing
LPCCS_CT12 | LAMAR POWER PARTNERS | NG | 153.8 | Existing
LPCCS_CT21 | LAMAR POWER PARTNERS | NG | 153.8 | Existing
LPCCS_CT22 | LAMAR POWER PARTNERS | NG | 153.8 | Existing
LPCCS_UNIT1 | LAMAR POWER PARTNERS | NG | 193.4 | Existing
LPCCS_UNIT2 | LAMAR POWER PARTNERS | NG | 193.4 | Existing
LARDVFTN_G4 | LAREDO ENERGY CENTER | NG | 94.2 | Existing
LARDVFTN_G5 | LAREDO ENERGY CENTER | NG | 94.2 | Existing
LEON_CRK_LCPCT1 | LEON CREEK | NG | 46 | Existing
LEON_CRK_LCPCT2 | LEON CREEK | NG | 46 | Existing
LEON_CRK_LCPCT3 | LEON CREEK | NG | 46 | Existing
LEON_CRK_LCPCT4 | LEON CREEK | NG | 46 | Existing
LEG_LEG_G1 | LIMESTONE PLANT | LIG | 831 | Existing
LEG_LEG_G2 | LIMESTONE PLANT | LIG | 858 | Existing
LOSTPI_LOSTPGT1 | LOST PINES | NG | 170 | Existing
LOSTPI_LOSTPGT2 | LOST PINES | NG | 170 | Existing
LOSTPI_LOSTPST1 | LOST PINES | NG | 188 | Existing
LFBIO_UNIT1 | LUFKIN BIOMASS | WDS | 45 | Existing
MLSES_UNIT1 | MARTIN LAKE SES | LIG | 800 | Existing
MLSES_UNIT2 | MARTIN LAKE SES | LIG | 805 | Existing
MLSES_UNIT3 | MARTIN LAKE SES | LIG | 805 | Existing
DG_MKNSW_2UNITS | MCKINNEY LANDFILL | LFG | 3.2 | Nonmod
DG_FREIH_2UNITS | MESQUITE CREEK LANDFILL | LFG | 3.2 | Nonmod
MDANP_CT1 | MIDLOTHIAN ANP | NG | 216 | Existing
MDANP_CT2 | MIDLOTHIAN ANP | NG | 216 | Existing
MDANP_CT3 | MIDLOTHIAN ANP | NG | 216 | Existing
MDANP_CT4 | MIDLOTHIAN ANP | NG | 216 | Existing
MDANP_CT5 | MIDLOTHIAN ANP | NG | 225 | Existing
MDANP_CT6 | MIDLOTHIAN ANP | NG | 225 | Existing
MIL_MILLERG1 | MILLER | NG | 75 | Existing
MIL_MILLERG2 | MILLER | NG | 120 | Existing
MIL_MILLERG3 | MILLER | NG | 208 | Existing
MIL_MILLERG4 | MILLER | NG | 104 | Existing
MIL_MILLERG5 | MILLER | NG | 104 | Existing
MNSES_UNIT1 | MONTICELLO SES | SUB | 535 | Existing
MNSES_UNIT2 | MONTICELLO SES | SUB | 535 | Existing
MNSES_UNIT3 | MONTICELLO SES | SUB | 795 | Existing
MGSES_CT1 | MORGAN CREEK SES | NG | 68 | Existing
MGSES_CT2 | MORGAN CREEK SES | NG | 68 | Existing
MGSES_CT3 | MORGAN CREEK SES | NG | 68 | Existing
MGSES_CT4 | MORGAN CREEK SES | NG | 68 | Existing
MGSES_CT5 | MORGAN CREEK SES | NG | 68 | Existing
MGSES_CT6 | MORGAN CREEK SES | NG | 67 | Existing
MCSES_UNIT6 | MOUNTAIN CREEK SES | NG | 120 | Existing
MCSES_UNIT7 | MOUNTAIN CREEK SES | NG | 115 | Existing
MCSES_UNIT8 | MOUNTAIN CREEK SES | NG | 565 | Existing
NEDIN_NEDIN_G1 | N EDINBURG | NG | 208.58 | Existing
NEDIN_NEDIN_G2 | N EDINBURG | NG | 208.58 | Existing
NEDIN_NEDIN_G3 | N EDINBURG | WH | 252.98 | Existing
NACPW_UNIT1 | NACOGDOCHES POWER | WDS | 105 | Existing
NWF_NBS | NoTrees Battery Storage | OTH | 33.7 | Existing
NUECES_B_NUECESG7 | NUECES BAY | NG | 319 | Existing
NUECES_B_NUECESG8 | NUECES BAY | NG | 157 | Existing
NUECES_B_NUECESG9 | NUECES BAY | NG | 157 | Existing
OGSES_UNIT1A | OAK GROVE SES | LIG | 840 | Existing
OGSES_UNIT2 | OAK GROVE SES | LIG | 825 | Existing
OCI_ALM1_UNIT1 | OCI ALAMO 1 | SUN | 39.183 | Existing
OECCS_CT11 | ODESSA ECTOR CCS | NG | 151 | Existing
OECCS_CT12 | ODESSA ECTOR CCS | NG | 140.4 | Existing
OECCS_CT21 | ODESSA ECTOR CCS | NG | 144.7 | Existing
OECCS_CT22 | ODESSA ECTOR CCS | NG | 142.4 | Existing
OECCS_UNIT1 | ODESSA ECTOR CCS | NG | 210 | Existing
OECCS_UNIT2 | ODESSA ECTOR CCS | NG | 210 | Existing
OKLA_OKLA_G1 | OKLAUNION | BIT | 650 | Existing
OLINGR_OLING_1 | OLINGER | NG | 78 | Existing
OLINGR_OLING_2 | OLINGER | NG | 107 | Existing
OLINGR_OLING_3 | OLINGER | NG | 146 | Existing
OLINGR_OLING_4 | OLINGER | NG | 75 | Existing
PSG_PSG_GT2 | PASGEN | NG | 164 | Existing
PSG_PSG_GT3 | PASGEN | NG | 164 | Existing
PSG_PSG_ST2 | PASGEN | WH | 167 | Existing
PEARSALL_PEARS_1 | PEARSALL | NG | 25 | Existing
PEARSALL_PEARS_2 | PEARSALL | NG | 25 | Existing
PEARSALL_PEARS_3 | PEARSALL | NG | 25 | Existing
PEARSAL2_AGR_A | PEARSALL POWER PLANT 2 | NG | 50.64 | Existing
PEARSAL2_AGR_B | PEARSALL POWER PLANT 2 | NG | 50.64 | Existing
PEARSAL2_AGR_C | PEARSALL POWER PLANT 2 | NG | 50.64 | Existing
PEARSAL2_AGR_D | PEARSALL POWER PLANT 2 | NG | 50.64 | Existing
PB2SES_CT1 | PERMIAN BASIN SES RELIANT | NG | 68 | Existing
PB2SES_CT2 | PERMIAN BASIN SES RELIANT | NG | 65 | Existing
PB2SES_CT3 | PERMIAN BASIN SES RELIANT | NG | 68 | Existing
PB2SES_CT4 | PERMIAN BASIN SES RELIANT | NG | 69 | Existing
PB2SES_CT5 | PERMIAN BASIN SES RELIANT | NG | 70 | Existing
QALSW_GT1 | QUAIL SWITCH | NG | 74 | Existing
QALSW_GT2 | QUAIL SWITCH | NG | 74 | Existing
QALSW_GT3 | QUAIL SWITCH | NG | 72 | Existing
QALSW_GT4 | QUAIL SWITCH | NG | 72 | Existing
QALSW_STG1 | QUAIL SWITCH | NG | 98 | Existing
QALSW_STG2 | QUAIL SWITCH | NG | 98 | Existing
RIONOG_CT1 | RIO NOGALES POWER PROJECT | NG | 154 | Existing
RIONOG_CT2 | RIO NOGALES POWER PROJECT | NG | 154 | Existing
RIONOG_CT3 | RIO NOGALES POWER PROJECT | NG | 154 | Existing
RIONOG_ST1 | RIO NOGALES POWER PROJECT | WH | 323 | Existing
RAYBURN_RAYBURG1 | SAM RAYBURN SWITCHYD | NG | 11 | Existing
RAYBURN_RAYBURG2 | SAM RAYBURN SWITCHYD | NG | 11 | Existing
RAYBURN_RAYBURG7 | SAM RAYBURN SWITCHYD | NG | 50 | Existing
RAYBURN_RAYBURG8 | SAM RAYBURN SWITCHYD | NG | 50 | Existing
RAYBURN_RAYBURG9 | SAM RAYBURN SWITCHYD | NG | 50 | Existing
RAYBURN_RAYBURG10 | SAM RAYBURN SWITCHYD | WH | 40 | Existing
SJS_SJS_G1 | SAN JACINTO STEAM | NG | 81 | Existing
SJS_SJS_G2 | SAN JACINTO STEAM | NG | 81 | Existing
SANMIGL_SANMIGG1 | SAN MIGUEL GEN | LIG | 391 | Existing
SANDHSYD_SH_5A | SANDHILL POWER STATION | NG | 150 | Existing
SANDHSYD_SH_5C | SANDHILL POWER STATION | NG | 145 | Existing
SANDHSYD_SH1 | SANDHILL POWER STATION | NG | 47 | Existing
SANDHSYD_SH2 | SANDHILL POWER STATION | NG | 47 | Existing
SANDHSYD_SH3 | SANDHILL POWER STATION | NG | 47 | Existing
SANDHSYD_SH4 | SANDHILL POWER STATION | NG | 47 | Existing
SANDHSYD_SH6 | SANDHILL POWER STATION | NG | 47 | Existing
SANDHSYD_SH7 | SANDHILL POWER STATION | NG | 47 | Existing
SD5SES_UNIT5 | SANDOW 5 SES | LIG | 570 | Existing
SCES_UNIT1 | SANDY CREEK | SUB | 970 | Existing
SILASRAY_SILAS_10 | SILAS RAY | NG | 46 | Existing
SILASRAY_SILAS_9 | SILAS RAY | NG | 38 | Existing
SILASRAY_SILAS_6 | SILAS RAY | WH | 20 | Existing
GIDEON_GIDEONG1 | SIM GIDEON | NG | 130 | Existing
GIDEON_GIDEONG2 | SIM GIDEON | NG | 135 | Existing
GIDEON_GIDEONG3 | SIM GIDEON | NG | 332 | Existing
DG_FERIS_4_UNITS | SKYLINE LANDFILL GAS | UNK | 6.4 | Nonmod
DG_SOME1_1UNIT | SOMERSET NORTH | SUN | 5.61 | Nonmod
DG_SOME2_1UNIT | SOMERSET SOUTH | SUN | 5 | Nonmod
STP_STP_G1 | SOUTH TEXAS PROJECT | NUC | 1375 | Existing
STP_STP_G2 | SOUTH TEXAS PROJECT | NUC | 1375 | Existing
SPNCER_SPNCE_4 | SPENCER | NG | 61 | Existing
SPNCER_SPNCE_5 | SPENCER | NG | 61 | Existing
SCSES_UNIT1A | STRYKER CREEK SES | NG | 167 | Existing
SCSES_UNIT2 | STRYKER CREEK SES | NG | 502 | Existing
DG_VALL1_1UNIT | SUNEDISON RABEL ROAD | SUN | 9.9 | Nonmod
DG_VALL2_1UNIT | SUNEDISON VALLEY ROAD | SUN | 9.9 | Nonmod
TEN_CT1 | TENASKA (BRAZOS) | NG | 163 | Existing
TEN_STG | TENASKA (BRAZOS) | WH | 106 | Existing
TNSKA_GT1 | TENASKA (TXU) | NG | 76 | Existing
TNSKA_GT2 | TENASKA (TXU) | NG | 76 | Existing
TNSKA_STG | TENASKA (TXU) | WH | 87 | Existing
DG_WALZE_4UNITS | TESSMAN ROAD | MTE | 9.78 | Nonmod
TXCTY_CTA | TEXAS CITY GEN | NG | 96.58 | Existing
TXCTY_CTB | TEXAS CITY GEN | NG | 96.58 | Existing
TXCTY_CTC | TEXAS CITY GEN | NG | 96.58 | Existing
TXCTY_ST | TEXAS CITY GEN | WH | 131.58 | Existing
TGF_TGFGT_1 | TEXAS GULF SULPHUR | NG | 79 | Existing
THW_THWGT_1 | TH WHARTON | NG | 13 | Existing
THW_THWGT31 | TH WHARTON | NG | 57 | Existing
THW_THWGT32 | TH WHARTON | NG | 57 | Existing
THW_THWGT33 | TH WHARTON | NG | 57 | Existing
THW_THWGT34 | TH WHARTON | NG | 57 | Existing
THW_THWGT41 | TH WHARTON | NG | 57 | Existing
THW_THWGT42 | TH WHARTON | NG | 57 | Existing
THW_THWGT43 | TH WHARTON | NG | 57 | Existing
THW_THWGT44 | TH WHARTON | NG | 57 | Existing
THW_THWGT51 | TH WHARTON | NG | 57 | Existing
THW_THWGT52 | TH WHARTON | NG | 57 | Existing
THW_THWGT53 | TH WHARTON | NG | 57 | Existing
THW_THWGT54 | TH WHARTON | NG | 57 | Existing
THW_THWGT55 | TH WHARTON | NG | 57 | Existing
THW_THWGT56 | TH WHARTON | NG | 57 | Existing
THW_THWST_3 | TH WHARTON | NG | 104 | Existing
THW_THWST_4 | TH WHARTON | NG | 104 | Existing
TNP_ONE_TNP_O_1 | TNP ONE PLANT | LIG | 156 | Existing
TNP_ONE_TNP_O_2 | TNP ONE PLANT | LIG | 156 | Existing
ETCCS_CT1 | TRACTEBEL | NG | 196 | Existing
ETCCS_UNIT1 | TRACTEBEL | NG | 116 | Existing
TRSES_UNIT6 | TRINIDAD SES | NG | 226 | Existing
DG_KLBRG_1UNIT | TRINITY OAKS LFG | LFG | 3.2 | Nonmod
BRAUNIG_AVR1_CT1 | VH BRAUNIG | NG | 155 | Existing
BRAUNIG_AVR1_CT2 | VH BRAUNIG | NG | 155 | Existing
BRAUNIG_VHB1 | VH BRAUNIG | NG | 220 | Existing
BRAUNIG_VHB2 | VH BRAUNIG | NG | 230 | Existing
BRAUNIG_VHB3 | VH BRAUNIG | NG | 412 | Existing
BRAUNIG_VHB6CT5 | VH BRAUNIG | NG | 48 | Existing
BRAUNIG_VHB6CT6 | VH BRAUNIG | NG | 48 | Existing
BRAUNIG_VHB6CT7 | VH BRAUNIG | NG | 48 | Existing
BRAUNIG_VHB6CT8 | VH BRAUNIG | NG | 48 | Existing
BRAUNIG_AVR1_ST | VH BRAUNIG | WH | 180 | Existing
VICTORIA_VICTORG6 | VICTORIA | NG | 160 | Existing
VICTORIA_VICTORG5 | VICTORIA | WH | 125 | Existing
WAP_WAP_G5 | WA PARISH | BIT | 659 | Existing
WAP_WAP_G6 | WA PARISH | BIT | 658 | Existing
WAP_WAP_G7 | WA PARISH | BIT | 577 | Existing
WAP_WAP_G8 | WA PARISH | BIT | 610 | Existing
WAP_WAP_G1 | WA PARISH | NG | 169 | Existing
WAP_WAP_G2 | WA PARISH | NG | 169 | Existing
WAP_WAP_G3 | WA PARISH | NG | 258 | Existing
WAP_WAP_G4 | WA PARISH | NG | 552 | Existing
WAP_WAPGT_1 | WA PARISH | NG | 13 | Existing
PNPI_GT2 | WA Parish Addition | NG | 74 | Existing
WEBBER_S_WSP1 | WEBBERVILLE | SUN | 28.5 | Existing
DG_WSTHL_3UNITS | WESTSIDE | LFG | 4.8 | Nonmod
WFCOGEN_UNIT1 | WICHITA FALLS COGEN SWITCH | NG | 20 | Existing
WFCOGEN_UNIT2 | WICHITA FALLS COGEN SWITCH | NG | 20 | Existing
WFCOGEN_UNIT3 | WICHITA FALLS COGEN SWITCH | NG | 20 | Existing
WFCOGEN_UNIT4 | WICHITA FALLS COGEN SWITCH | WH | 17 | Existing
WIPOPA_WPP_G1 | WINCHESTER POWER PARK | NG | 44 | Existing
WIPOPA_WPP_G2 | WINCHESTER POWER PARK | NG | 44 | Existing
WIPOPA_WPP_G3 | WINCHESTER POWER PARK | NG | 44 | Existing
WIPOPA_WPP_G4 | WINCHESTER POWER PARK | NG | 44 | Existing
WCPP_CT1 | WISE COUNTY POWER PLANT | NG | 212 | Existing
WCPP_CT2 | WISE COUNTY POWER PLANT | NG | 212 | Existing
WCPP_ST1 | WISE COUNTY POWER PLANT | NG | 241 | Existing
WHCCS_CT1 | WOLF HOLLOW GEN | NG | 212.5 | Existing
WHCCS_CT2 | WOLF HOLLOW GEN | NG | 212.5 | Existing
WHCCS_STG | WOLF HOLLOW GEN | WH | 280 | Existing
| Total Existing Resources |  | 64547.129
AMISTAD_AMISTAG1 | AMISTAD | WAT | 37.9 | Existing
AMISTAD_AMISTAG2 | AMISTAD | WAT | 37.9 | Existing
AUSTPL_AUSTING1 | AUSTIN PLANT | WAT | 8 | Existing
AUSTPL_AUSTING2 | AUSTIN PLANT | WAT | 9 | Existing
BUCHAN_BUCHANG1 | BUCHANAN | WAT | 16 | Existing
BUCHAN_BUCHANG2 | BUCHANAN | WAT | 16 | Existing
BUCHAN_BUCHANG3 | BUCHANAN | WAT | 17 | Existing
CANYHY_CANYHYG1 | CANYON | WAT | 6 | Nonmod
DNDAM_DENISOG1 | DENISON DAM | WAT | 40 | Existing
DNDAM_DENISOG2 | DENISON DAM | WAT | 40 | Existing
DG_SCHUM_2UNITS | DUNLOP (SCHUMANSVILLE) | WAT | 3.6 | Nonmod
EAGLE_HY_EAGLE_HY1 | EAGLE PASS | WAT | 9.6 | Nonmod
FALCON_FALCONG1 | FALCON PLANT | WAT | 12 | Existing
FALCON_FALCONG2 | FALCON PLANT | WAT | 12 | Existing
FALCON_FALCONG3 | FALCON PLANT | WAT | 12 | Existing
DG_LKWDT_2UNITS | GBRA | WAT | 4.8 | Nonmod
INKSDA_INKS_G1 | INKS DAM | WAT | 14 | Existing
DG_LWSVL_1UNIT | LEWISVILLE | WAT | 2.2 | Nonmod
MARBFA_MARBFAG1 | MARBLE FALLS | WAT | 21 | Existing
MARBFA_MARBFAG2 | MARBLE FALLS | WAT | 20 | Existing
MARSFO_MARSFOG1 | MARSHALL FORD | WAT | 36 | Existing
MARSFO_MARSFOG2 | MARSHALL FORD | WAT | 36 | Existing
MARSFO_MARSFOG3 | MARSHALL FORD | WAT | 29 | Existing
DG_MCQUE_5UNITS | MCQUEENEY (ABBOTT) | WAT | 7.7 | Nonmod
WND_WHITNEY2 | WHITNEY DAM | WAT | 15 | Existing
WIRTZ_WIRTZ_G1 | WIRTZ | WAT | 29 | Existing
WIRTZ_WIRTZ_G2 | WIRTZ | WAT | 29 | Existing
| Total Hydro Resources |  | 520.7
Hydro Capacity Contribution (Average maximum capability for Top 20 Hours) |  |  | 446.2
WCSOLAR1_100PV | WHITE CAMP SOLAR | SUN | 100 | Planned
HOVEY_UNIT1 | PECOS BARILLA SOLAR | SUN | 30 | Planned
| Total Planned non-Wind Resources |  | 130
PUN AGGREGATE | PUN OUTPUT TO GRID | OTH | 4655 | PUN
| Total Private Use Networks |  | 4655
FTR_FTR_G1 | FRONTIER | NG | 165 | Switchable
FTR_FTR_G2 | FRONTIER | NG | 165 | Switchable
FTR_FTR_G3 | FRONTIER | NG | 165 | Switchable
KMCHI_1CT101 | KIAMICHI ENERGY FACILITY | NG | 153 | Switchable
KMCHI_1CT201 | KIAMICHI ENERGY FACILITY | NG | 155 | Switchable
KMCHI_2CT101 | KIAMICHI ENERGY FACILITY | NG | 153 | Switchable
KMCHI_2CT201 | KIAMICHI ENERGY FACILITY | NG | 155 | Switchable
TGCCS_CT1 | TENASKA GATEWAY | NG | 156 | Switchable
TGCCS_CT2 | TENASKA GATEWAY | NG | 135 | Switchable
TGCCS_CT3 | TENASKA GATEWAY | NG | 153 | Switchable
FTR_FTR_G4 | FRONTIER | WH | 390 | Switchable
KMCHI_1ST | KIAMICHI ENERGY FACILITY | WH | 315 | Switchable
KMCHI_2ST | KIAMICHI ENERGY FACILITY | WH | 315 | Switchable
TGCCS_UNIT4 | TENASKA GATEWAY | WH | 402 | Switchable
| Total Switchable Resources |  | 2977
ANACACHO_ANA | Anacacho Windfarm | WND | 101 | Wind
BLSUMMIT_BLSMT1_5 | Blue Summit Windfarm 1 | WND | 9 | Wind
BLSUMMIT_BLSMT1_6 | Blue Summit Windfarm 2 | WND | 126.4 | Wind
BRAZ_WND_WND1 | Green Mountain Energy 1 | WND | 99 | Wind
BRAZ_WND_WND2 | Green Mountain Energy 2 | WND | 61 | Wind
BRTSW_BCW1 | Barton Chapel Wind | WND | 120 | Wind
BCATWIND_WIND_1 | Bobcat Bluff | WND | 150 | Wind
BUFF_GAP_UNIT1 | Buffalo Gap Wind Farm 1 | WND | 120.6 | Wind
BUFF_GAP_UNIT2_1 | Buffalo Gap Wind Farm 2 | WND | 115.5 | Wind
BUFF_GAP_UNIT2_2 | Buffalo Gap Wind Farm 2 | WND | 117 | Wind
BUFF_GAP_UNIT3 | Buffalo Gap Wind Farm 3 | WND | 170.2 | Wind
BULLCRK_WND1 | Bull Creek Wind Plant | WND | 88 | Wind
BULLCRK_WND2 | Bull Creek Wind Plant | WND | 90 | Wind
CAPRIDG4_CR4 | Capricorn Ridge Wind 4 | WND | 112.5 | Wind
CAPRIDGE_CR1 | Capricorn Ridge Wind 1 | WND | 214.5 | Wind
CAPRIDGE_CR2 | Capricorn Ridge Wind 3 | WND | 149.5 | Wind
CAPRIDGE_CR3 | Capricorn Ridge Wind 2 | WND | 186 | Wind
CEDROHIL_CHW1 | Cedro Hill Wind | WND | 150 | Wind
CHAMPION_UNIT1 | Champion Wind Farm | WND | 126.5 | Wind
CSEC_CSECG1 | Camp Springs 1 | WND | 130.5 | Wind
CSEC_CSECG2 | Camp Springs 2 | WND | 120 | Wind
DG_ROSC2_1UNIT | TSTC West Texas Wind | WND | 2 | Wind
ELB_ELBCREEK | Elbow Creek Wind Project | WND | 118.7 | Wind
ENAS_ENA1 | Snyder Wind Farm | WND | 63 | Wind
EXGNWTL_WIND_1 | Whitetail Wind Energy Project | WND | 90 | Wind
FLTCK_SSI | Silver Star | WND | 60 | Wind
GOAT_GOATWIN2 | Goat Wind 2 | WND | 69.6 | Wind
GOAT_GOATWIND | Goat Wind | WND | 80 | Wind
CALLAHAN_WND1 | Horse Hollow Wind Callahan | WND | 114 | Wind
H_HOLLOW_WND1 | Horse Hollow Wind 1 | WND | 213 | Wind
HHOLLOW2_WIND1 | Horse Hollow Wind 2 | WND | 184 | Wind
HHOLLOW3_WND_1 | Horse Hollow Wind 3 | WND | 223.5 | Wind
HHOLLOW4_WND1 | Horse Hollow Wind 4 | WND | 115 | Wind
HWF_HWFG1 | Hackberry Wind Farm | WND | 163.5 | Wind
INDL_INADALE1 | Inadale Wind | WND | 196.6 | Wind
INDNENR_INDNENR | Desert Sky Wind Farm 1 | WND | 84 | Wind
INDNENR_INDNENR_2 | Desert Sky Wind Farm 2 | WND | 76.5 | Wind
INDNNWP_INDNNWP | Indian Mesa Wind Farm | WND | 82.5 | Wind
KEO_KEO_SM1 | Sherbino I | WND | 150 | Wind
KEO_SHRBINO2 | Sherbino 2 | WND | 150 | Wind
KING_NE_KINGNE | King Mountain NE | WND | 79.3 | Wind
KING_NW_KINGNW | King Mountain NW | WND | 79.3 | Wind
KING_SE_KINGSE | King Mountain SE | WND | 40.3 | Wind
KING_SW_KINGSW | King Mountain SW | WND | 79.3 | Wind
KUNITZ_WIND_LGE | Kunitz Wind | WND | 39.8 | Wind
KUNITZ_WIND_NWP | Delaware Mountain Wind Farm | WND | 28.5 | Wind
LGD_LANGFORD | Langford Wind Power | WND | 155 | Wind
LNCRK_G83 | Mesquite Wind | WND | 200 | Wind
LNCRK2_G871 | Post Oak Wind 1 | WND | 100 | Wind
LNCRK2_G872 | Post Oak Wind 2 | WND | 100 | Wind
LONEWOLF_G1 | Loraine Windpark I | WND | 49.5 | Wind
LONEWOLF_G2 | Loraine Windpark II | WND | 51 | Wind
LONEWOLF_G3 | Loraine Windpark III | WND | 25.5 | Wind
LONEWOLF_G4 | Loraine Windpark IV | WND | 24 | Wind
MCDLD_FCW1 | Forest Creek Wind Farm | WND | 124.2 | Wind
MCDLD_SBW1 | Sand Bluff Wind Farm | WND | 90 | Wind
MOZART_WIND_1 | WKN Mozart | WND | 30 | Wind
MWEC_G1 | McAdoo Wind Farm | WND | 150 | Wind
NWF_NWF1 | Notrees-1 | WND | 92.6 | Wind
NWF_NWF2 | Notrees-2 | WND | 60 | Wind
OWF_OWF | Ocotillo Wind Farm | WND | 58.8 | Wind
PC_NORTH_PANTHER1 | Panther Creek 1 | WND | 142.5 | Wind
PC_SOUTH_PANTHER2 | Panther Creek 2 | WND | 115.5 | Wind
PC_SOUTH_PANTHER3 | Panther Creek 3 | WND | 199.5 | Wind
PYR_PYRON1 | Pyron Wind Farm | WND | 249 | Wind
RDCANYON_RDCNY1 | Red Canyon | WND | 84 | Wind
SENATEWD_UNIT1 | Senate Wind Project | WND | 150 | Wind
SGMTN_SIGNALMT | Texas Big Spring | WND | 34.32 | Wind
STWF_T1 | South Trent Wind Farm | WND | 101.2 | Wind
SW_MESA_SW_MESA | West Texas Wind Energy | WND | 74.2 | Wind
SWEC_G1 | Stanton Wind Energy | WND | 120 | Wind
SWEETWN2_WND2 | Sweetwater Wind 3 | WND | 97.5 | Wind
SWEETWN2_WND24 | Sweetwater Wind 2 | WND | 15.87 | Wind
SWEETWN3_WND3A | Sweetwater Wind 4 | WND | 28.5 | Wind
SWEETWN3_WND3B | Sweetwater Wind 4 | WND | 100.5 | Wind
SWEETWN4_WND4A | Sweetwater Wind 7 | WND | 117.8 | Wind
SWEETWN4_WND4B | Sweetwater Wind 6 | WND | 103.65 | Wind
SWEETWN4_WND5 | Sweetwater Wind 5 | WND | 79.23 | Wind
SWEETWND_WND1 | Sweetwater Wind 1 | WND | 36.58 | Wind
TKWSW1_ROSCOE | Roscoe Wind Farm | WND | 209 | Wind
TRENT_TRENT | Trent Wind Farm | WND | 150 | Wind
TRINITY_TH1_BUS1 | Trinity Hills | WND | 117.5 | Wind
TRINITY_TH1_BUS2 | Trinity Hills | WND | 107.5 | Wind
TTWEC_G1 | Turkey Track Wind Energy Center | WND | 169.5 | Wind
WEC_WECG1 | Whirlwind Energy | WND | 56.957 | Wind
WHTTAIL_WR1 | Wolfe Ridge | WND | 112.5 | Wind
WOODWRD1_WOODWRD1 | Pecos Wind (Woodward 1) | WND | 82.5 | Wind
WOODWRD2_WOODWRD2 | Pecos Wind (Woodward 2) | WND | 77.22 | Wind
COTTON_PAP2 | Papalote Creek Wind | WND | 200.1 | Wind*
DG_NUECE_6UNITS | Harbor Wind | WND | 9 | Wind*
LV1_LV1B | Los Vientos 1 | WND | 201.6 | Wind*
LV1_LV1A | Los Vientos 2 | WND | 200.1 | Wind*
PAP1_PAP1 | Papalote Creek Wind Farm | WND | 179.85 | Wind*
PENA_UNIT1 | Penascal Wind | WND | 160.8 | Wind*
PENA_UNIT2 | Penascal Wind | WND | 141.6 | Wind*
PENA3_UNIT3 | Penascal Wind | WND | 100.8 | Wind*
REDFISH_MV1A | Magic Valley Wind | WND | 103 | Wind*
REDFISH_MV1B | Magic Valley Wind | WND | 103 | Wind*
TGW_T1 | Gulf Wind I | WND | 141.6 | Wind*
TGW_T2 | Gulf Wind II | WND | 141.6 | Wind*
| Total Wind Resources |  | 11065.777
SSPURTWO_WIND_1 | SPINNING SPUR WIND TWO | WND | 161 | Planned
| Total New wind Resources |  | 161
* Coastal Wind
Note: Capacity Information is current as of 2/17/2014

## Background
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Background
The Seasonal Assessment of Resource Adequacy (SARA) report is a deterministic approach to considering the impact of potential variables that may affect the sufficiency of installed resources to meet the peak electrical demand on the ERCOT System during a particular season.
The standard approach to assessing resource adequacy for one or more years into the future is to account for projected load and resources on a normalized basis and to require sufficient reserves (resources in excess of peak demand, on this normalized basis) to cover the uncertainty in peak demand and resource availability to meet a one-in-ten-years loss-of-load event criteria on a probabilistic basis.
For seasonal assessments that look ahead less than a year, specific information may be available (such as seasonal climate forecasts or anticipated common-mode events such as drought) which can be used to consider the range of resource adequacy in a more deterministic manner.
The SARA report is intended to illustrate the range of resource adequacy outcomes that might occur, and thus help fulfill the reporting requirement per Public Utility Commission of Texas rule 25.362(i)(2)(H). Several sensitivity analyses are developed by varying the value of certain parameters that affect resource adequacy. The variation in these parameters is either based on historic values of these parameters, adjusted by any known or expected change.