## Slide 1: PDCWG Report to ROS
David Kee Chair
CPS Energy
Sydney Niemeyer Vice Chair
NRG Energy

## Slide 2: February Meeting
Leadership nomination change from January nomination.
Frequency Event Review

## Slide 3: PDCWG Leadership – 2014
Chair – Sydney Niemeyer
Vice Chair – Don Blackburn

## Slide 4: ERCOT Frequency Control Report February 2014
Sydney Niemeyer NRG Energy
March 3, 2014

## Slide 5: Notes
Time error values from NRG True Time device can be slightly different from ERCOT’s Time Error but the daily delta times should be accurate.

## Slide 6: Ercot frequency control
BAL-001 CPS 1 & 2 Performance, RMS 1 and Frequency Profile

## Slide 9
CPS1 12 Month Rolling Average = 164.76

## Slide 14
60.010 <= HZ < 60.015

## Slide 16: ERCOT Time error and time correction
Time Error History

## Slide 17: Time Error Corrections
Six slow Time Error Corrections were executed in January.
Other than the days with the TECs, only 4 days had positive time error.

## Slide 20
Time Correction History

## Slide 23: Ercot primary frequency response performance
BAL-003-1 Interconnection Frequency Response and Bias Measure.

## Slide 24
ERCOT Primary Frequency Response – BAL-003-1
2015 Bias and Frequency Response Measure

## Slide 25: Ercot total energy and wind production
October Total ERCOT Energy and Total Energy Production from Wind Resources.