System Operating Limit Methodology for

Planning and Operations Horizon

Effective Date: March 1, 2014

© 2013 Electric Reliability Council of Texas, Inc.

© 2013 Electric Reliability Council of Texas, Inc.

Index of Contents

1.	Purpose............................................................................................................................................. 3

2.	Definitions........................................................................................................................................ 3 3.	SOL/IROL Determination Methodology .................................................................................... 4

3.1.	Transmission Planner SOLs ................................................................................................... 5

3.2.	Transmission Operator SOLs ................................................................................................. 5

3.3 	Steady State Voltage SOLs......................................................................................................... 5

3.4.	System Assessment and General Performance Criteria........................................................ 5

3.5.	Study Modeling and Criteria................................................................................................... 7

3.6.	Determination Criteria ............................................................................................................ 10

3.7.	Load Loss Threshold Guidelines............................................................................................ 11

4.	Distribution...................................................................................................................................... 11

5. 	Document Revisions....................................................................................................................... 13

1. Purpose

NERC  standard  FAC-010-2.1 R1 requires  that  each  Planning  Authority (PA)  “shall  have  a  documented  System Operating Limit (SOL) Methodology for use in developing SOLs within its Planning Authority Area” for the planning horizon.  NERC standards FAC-011-2 R1 requires that each Reliability Coordinator (RC) “shall have a documented methodology for use in developing SOLs (SOL Methodology) within its Reliability Coordinator Area” for the operations horizon. This document describes the methodology for determining the SOLs, and the subset of SOLs classified as Interconnection Reliability Operating Limits (IROLs), for the planning horizon and operations horizon within the ERCOT Interconnection [FAC-010-2.1 R1.1, R1.3; FAC-011-2 R1.1, R1.3]. This methodology also documents the communications with other interested and affected organizations [FAC-014-2 R5, R6].

This methodology is intended to address NERC Reliability Standard requirements and does not restrict any entity from applying more conservative or alternative means to determine SOLs as needed to meet any additional regulatory requirements.

2. Definitions

Where a NERC defined term exists, it is used in this document for that purpose. The NERC Glossary of Terms Used in Reliability Standards provides the following definitions:

Bulk Electric System (BES):

As defined by the Regional Reliability Organization, the electrical generation resources, transmission lines, interconnections with neighboring systems, and associated equipment, generally operated at

voltages of 100 kV or higher. Radial transmission facilities serving only load with one transmission

source are generally not included in this definition

Emergency Rating:

The rating as defined by the equipment owner that specifies the level of electrical loading or output, usually expressed in megawatts (MW) or Mvar or other appropriate units, that a system, facility, or element can support, produce, or withstand for a finite period. The rating assumes acceptable loss of equipment life or other physical or safety limitations for the equipment involved.

Facility:

A set of electrical equipment that operates as a single Bulk Electric System Element (e.g., a line, a generator, a shunt compensator, transformer, etc.)

Facility Rating:

The maximum or minimum voltage, current, frequency, or real or reactive power flow through a facility that does not violate the applicable equipment rating of any equipment comprising the facility.

Interconnection Reliability Operating Limit (IROL):

A System Operating Limit that, if violated, could lead to instability, uncontrolled separation, or Cascading Outages that adversely impact the reliability of the Bulk Electric System.

Interconnection Reliability Operating Limit Tv (IROL Tv):

The maximum time that an Interconnection Reliability Operating Limit can be violated before the risk to the interconnection or other Reliability Coordinator Area(s) becomes greater than acceptable. Each Interconnection Reliability Operating Limit’s Tv shall be less than or equal to 30 minutes.

Normal Rating:

The rating as defined by the equipment owner that specifies the level of electrical loading, usually expressed in megawatts (MW) or other appropriate units that a system, facility, or element can support or withstand through the daily demand cycles without loss of equipment life.

System Operating Limit (SOL):

The value (such as MW, MVar, Amperes, Frequency or Volts) that satisfies the most limiting of the prescribed operating criteria for a specified system configuration to ensure operation within acceptable reliability criteria. System Operating Limits are based upon certain operating criteria. These include, but are not limited to:

  - Facility Ratings (Applicable pre- and post-Contingency equipment or facility ratings)

  - Transient Stability Ratings (Applicable pre- and post-Contingency Stability Limits)

  - Voltage Stability Ratings (Applicable pre- and post-Contingency Voltage Stability)

  - System Voltage Limits (Applicable pre- and post-Contingency Voltage Limits)

3. SOL/IROL Determination Methodology

This methodology is applicable for determining SOLs/IROLs used in the planning horizon and operations horizon.  Determination is made by assessing the reliability of the currently planned ERCOT transmission system for the planning horizon and the expected topology of the ERCOT transmission system for the operations horizon.  The assessment is accomplished through steady-state power flow, voltage stability, and transient stability analysis.

SOLs in the planning horizon are the most limiting of the prescribed operating criteria for a specified system configuration to ensure operation within the reliability criteria described in the NERC Transmission Planning (TPL) standards. SOLs in the operations horizon shall always equal Facility Ratings unless studies have established a more restrictive limit based on operational conditions. Facility Ratings determine the fundamental limits of transmission system equipment. An SOL shall not exceed the associated Facility Rating [FAC-010-2.1 R1.2, FAC-011-2 R1.2]. Other factors, such as a transient or voltage stability limit, may lead to an SOL that is more limiting than the Facility Rating.

The IROLs for the planning horizon and operations horizon relate to specific system configurations or defined system conditions (demand level, generation pattern, transfer amount, and Facility contingency conditions) for which instability, uncontrolled separation, or Cascading outages are projected to occur as described in Section 3 of this methodology.

3.1. Transmission Planner SOLs

Transmission Planners (TPs) provide SOLs to ERCOT ISO (acting as the Planning Authority (PA)).  SOLs provided include all known Facility Ratings, any known special transfer limits, and any stability limits that the TP has derived.  In accordance with this methodology, the TPs will also identify any SOLs they believe qualify as IROLs, based on the criteria identified in section 3.6 of this methodology.  All limits provided to the PA by the TPs will be included in the analysis described in section 3.4 of this methodology.

3.2. Transmission Operator SOLs

Transmission Operators (TOPs) that own transmission facilities shall provide all known information to ERCOT ISO regarding the following:  Facility Ratings, any special transfer limits, and any stability limits.  ERCOT ISO shall establish SOLs and IROLs, based on the information provided by the Transmission Operators and ERCOT ISO’s analysis described in section 3 of this methodology.  Transmission Operators shall notify ERCOT ISO of known system conditions that may affect SOLs and IROLs.

3.3. Steady State Voltage SOLs

3.3.1	Planning Steady State Voltage SOLs

The following voltage ranges are considered to be the steady state voltage SOLs in ERCOT:

(1) 0.95 per unit to 1.05 per unit in the pre-contingency state (and with all facilities in service in the planning horizon)

(2) 0.90 per unit to 1.05 per unit in the post-contingency state (following a NERC Category B or C contingency (where appropriate)

If a Facility owner has communicated to ERCOT ISO that a Facility has unique characteristics and may operate outside of the above ranges (e.g. Facilities located near a series capacitor) or that the Facility needs to be operated in a more restrictive range (e.g. a nuclear plant) then the Facility owner’s specified limits will be considered the steady state voltage SOLs for those unique Facilities.

TPs may plan their portion of the ERCOT Interconnection utilizing different steady state voltage SOLs but must communicate those steady state voltage SOLs to ERCOT ISO.

3.3.2	Operations Steady State Voltage SOLs

The following voltage ranges are considered to be the steady state voltage SOLs in ERCOT for Operations purposes:

(1) 0.95 per unit to 1.05 per unit in the pre-contingency state

(2) 0.90 per unit to 1.10 per unit in the post-contingency state.

If a Facility owner has communicated to ERCOT ISO alternate values, then the Facility owner’s specified limits will be considered the steady state voltage SOLs for their Facilities.

3.4. System Assessment and General Performance Criteria

The system assessment and general performance criteria identified in this section should be the same for both planning and operations horizon unless otherwise noted below.

As required by NERC Reliability Standard TPL-001, in the pre-contingency state and with all facilities in service (planning horizon), the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage, and stability limits. In the determination of SOLs, the BES condition used shall reflect expected system conditions and shall reflect changes to system topology such as Facility outages [FAC-010-2.1R2.1; FAC-011-2 R2.1].

As required by NERC Reliability Standard TPL-002, starting with all Facilities in service (planning horizon2),  and following any of the contingencies identified for NERC Reliability Standard TPL-002, the system  shall  demonstrate  transient,  dynamic  and  voltage  stability;  all  facilities  shall  be operating within their Facility Ratings and within their thermal, voltage and stability limits; and cascading or uncontrolled separation shall not occur.  The contingencies also include shunt devices and bipolar high voltage direct current systems not specifically included in TPL-002 Category B contingencies.  [FAC-010-2.2 R2.2.1, R2.2.2, R2.2.3; FAC-011-2 R2.2, R2.2.1, R2.2.2, R2.2.3]. Starting with all Facilities in service (planning horizon2), the system’s response to a single contingency may include any of the following [FAC-010-2.1 R2.3; FAC-011-2 R2.3]:

- Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the faulted Facility or by the affected area [FAC-010-2.1 R2.3.1; FAC-011-2 R2.3.1].

- System reconfiguration through manual or automatic control or protection actions [FAC-010-2.1 R2.3.2; FAC-011-2 R2.3.3].

For the operations horizon, the system’s response to a single contingency may also include any of the following [FAC-011-2 R2.3]:

- Interruption of other network customers;

(a) only if the system has already been adjusted, or is being adjusted, following at least one prior outage, or

(b) if the real-time operating conditions are more adverse than anticipated in the corresponding studies [FAC-011-2 R2.3.2].

To prepare for the next contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology [FAC-010-2.1 R2.4; FAC-011-2 R2.4].

As required by NERC Reliability Standard TPL-003, in the planning horizon, starting with all Facilities in service (planning horizon2),  and following any of the contingencies identified in NERC Reliability Standard TPL-003, the system shall demonstrate transient, dynamic and voltage stability; all facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and cascading  or  uncontrolled  separation  shall  not  occur  [FAC-010-2.1  R2.5].  The system’s response may include any of the following [FAC-010-2.1 R2.6]:

- Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the faulted Facility or by the affected area [FAC-010-2.1 R2.3.1].

- System reconfiguration through manual or automatic control or protection actions [FAC-010-2.1 R2.3.2]

- Planned or controlled interruption of electric supply to customers (load shedding), the planned removal from service of certain generators, and/or the curtailment of contracted firm (non-recallable reserved) electric power transfers [FAC-010-2.1 R2.6.1].  It should be noted that there are no firm transfers within the ERCOT Interconnection.

3.5. Study modeling and conditions

Planning Horizon:

Study cases published by the ERCOT Steady State Working Group (SSWG), ERCOT Dynamics Working Group (DWG) or ERCOT Regional Transmission Plan are used for planning horizon assessments [FAC-010-2.1 R3.1]. These cases will contain the best estimate of any planned transmission line maintenance outages, system configuration, anticipated generation dispatch, and load levels. Additional system conditions, such as a minimum load case or high wind / low load case, may also be studied if needed. [FAC-010-2.1 R3.5]. The study of additional system conditions, such as a higher load level, may provide additional reliability margin to the study cases selected.

The study models used in planning horizon analyses represent the entire ERCOT Transmission system, including all Facilities 60 kV and above.  The ERCOT Transmission system has a limited amount of flow capability between ERCOT and other Interconnections, all through DC-ties.  Therefore, ERCOT ISO models these interconnections in the base case data sets as generation or load using historical flow information. The level of detail in the system models used in the analysis is consistent with the SSWG and DWG manuals and processes [FAC-010-2.1 R3.1, R3.3]. The 60 kV and above threshold provides reliability margin to the study model that is above required obligations.

The contingencies selected for planning horizon analyses reference NERC TPL Standards as a minimum analysis criteria [FAC-010-2.1R3.2].

Where appropriate, simulations of Special Protection System (SPS) actions are allowed and may be included in the studies.  Inclusion of specific SPS actions will be determined by the impact the SPS would have on Facilities in the studies e.g. (If an SPS is not in the area and does not impact a Facility in the area, it would not be included).  Also, if the impact of the SPS does not affect the type of limit being determined, it may not be included [FAC-010-2.1 R3.4].

Operations Horizon:

The ERCOT ISO uses several different types of models in the operations horizon based on the study type.  The following applies to ERCOT ISO.

The Network Operations Model is the primary model used in the operations horizon.  The SSWG case may be used to conduct steady state studies in operations planning horizon (seasonal and beyond up to one year). The DWG case modeling information may be used to provide dynamic modeling data into the Transient Security Assessment Tool (TSAT). The Network Operations Model, SSWG, and DWG cases have the known current or expected system topology modeled for the ERCOT Interconnection Bulk Electric System (BES), and includes non-radial facilities 60 kV and above within the ERCOT Transmission system [FAC-011-2 R3.1, R3.4].  The 60 kV and above threshold provides additional reliability margin to the study model as it goes beyond the 100kV BES definition.

The ERCOT ISO’s Network Operations Model consists of transmission lines, autotransformers, circuit breakers and switches, reactive devices, generation facilities and step-up transformers, loads, and other relevant electrical components. The DWG study cases consist of similar information as mentioned above as well as additional details and modeling information necessary to perform dynamic and transient stability studies. The Network Operations Model, SSWG cases, and DWG cases are study models that are used to determine SOLs in the operations horizon [FAC-011-2 R3.1, R3.4].

The topology used in Energy Management System (EMS) applications, including the Study Network Analysis (STNET) application, is capable of using dynamic, temperature-adjusted ratings for specified transmission lines which Transmission Owners (TOs)/TOPs have previously identified through Network Operations Model Change Requests. Real-Time applications and tools will use the dynamic ratings, either through use of actual temperature information or telemetry received from the TOs/TOPs. The dynamic ratings of these lines are the SOLs unless otherwise limited by special transfer limits or stability limits. Future studies, based on the Network Operations Model, may use dynamic ratings based on expected weather conditions. [FAC-011-2 R3.4].

The contingency list used in the operations horizon includes, as a minimum, all non-radial BES transmission lines and BES transformers with a high side winding greater than 100 kV and at least one secondary winding greater than 100kV, and all BES generation facilities. Two transmission lines sharing the same tower for longer than 0.5 mile are modeled as a relevant system contingency. ERCOT ISO defines transmission line contingencies for all non-radial line segments that make up the circuit between two or more fault relaying breakers/disconnect switches located at two or more switching stations. Similarly, contingencies for autotransformers are defined for the autos and their corresponding fault relaying breakers. [FAC-011-2 R3.2].

ERCOT ISO considers actual or expected system conditions for the future operations time horizon and compares this with the planning horizon conditions studied to determine if a stability limit identified in the planning horizon is applicable in the operations horizon.  Any multiple contingencies associated with the stability limits are reviewed as part of the study that identified the stability limits, through coordination between planning and operations, to determine if they are credible multiple contingencies in the operations horizon.  ERCOT ISO considers other currently used credible multiple contingencies in the operations horizon as a basis for inclusion in the list of associated multiple contingencies related to the stability limit.  The credible multiple contingencies (associated with the stability limits), that were determined to be applicable in the operations horizon, are modeled and or modified as necessary.  Stability limits associated with more than one transmission element are modeled in the Network Model as an interface (a set of transmission lines whose flow is aggregated).  The numeric values of the limits are calculated and or updated prior to studies that utilize the limits, as necessary, due to study conditions that would potentially invalidate the previously calculated limits. [FAC-011-2 R3.3, R3.3.1].

Contingencies identified during the review for operations horizon are monitored in Real-Time using Real-Time applications and tools. ERCOT ISO uses Voltage Security Assessment Tool (VSAT) and TSAT in Real-Time to determine and monitor stability limits and stability limit SOLs.  Reliability margins are established for stability limit SOLs through off-line studies and or operational experience, and applied in Real-Time.  These reliability margins are intended to allow time to respond to potential exceedances with the intent of avoiding an exceedance of identified stability limits.

When using an SSWG case, and where appropriate, simulations of SPS actions are allowed and included in the studies.  This would be determined by the impact the SPS would have on Facilities in the studies e.g. (If an SPS is not in the area and does not impact a Facility in the area, it would not be included.)  If the impact of the SPS does not affect the type of limit being determined, it may not be included.  When using the Network Operations Model as the study case, SPSs are always evaluated as they are modeled as part of the Network Operations Model, unless the SPS is in outage. SPSs are allowed in Voltage Security Analysis Tool (VSAT) and Transient Security Analysis Tool (TSAT) as needed. [FAC-011-2 R3.5].

Anticipated topology, generation dispatch and load levels are utilized in performing studies in the operations horizon.  Anticipated topology is incorporated by including planned transmission and resource outages into the study cases, where appropriate.  Generation dispatch is incorporated by using a typical generation dispatch pattern for a particular load level for studies up to Real-Time.  Generation dispatch may also be incorporated by using Current Operating Plans (COPs) which are required to be provided by Generator Operators (GOPs) from Real-Time through seven days in the future.  Current Operating Plans are updated as necessary.  Load levels are incorporated by using historical loads and load forecasts as appropriate.  Reliability margins may be applied by using a conservative load forecast, conservative historical load, or by biasing the load forecast in a conservative fashion as appropriate.  Operating reserves also provide additional reliability margin to account for unplanned outages and forecast error [FAC-011-2 R3.6].

3.6. Determination Criteria

Based on the assessment results in section 3.4, additional SOLs are identified if the system performance results in any of the following:

    - Transient, dynamic instability (resulting in the loss of a generator due to the instability);

    - Voltage instability (resulting in uncontrolled voltage collapse);

    - Cascading or uncontrolled separation;

    - Voltage stability margin in the planning horizon is not sufficient to maintain post-transient voltage stability under the following two conditions for an ERCOT or TP-defined area:

      - A 5% increase in Load above expected peak supplied from resources external to the ERCOT or TP-defined area and NERC Category A or B operating conditions; or

      - A 2.5% increase in Load above expected peak supplied from resources external to the ERCOT or TP-defined area and NERC Category C operating conditions;

    - Post disturbance frequency outside the range from 59.4 Hz to 60.4 Hz; or

    - Manual system adjustments, such as system reconfiguration between contingencies in an N-1-1 Category C event, or load shedding are needed in order to prevent Cascading or transient, dynamic, or voltage instability.

ERCOT ISO, the TPs, or the TOPs may deviate from these criteria as necessary but should justify the reasoning for such deviation and the deviation should maintain or improve system reliability.

An SOL is an IROL if the system performance response results in:

    - Loss of load in the Cascading or voltage collapse, either through manual action or as a consequence of the event (including loss of load as a result of Under Voltage Load Shedding (UVLS), is greater than a threshold as defined in section 3.7 of this methodology.

- Trigger of automatic under frequency load shedding

- Observable inter-area oscillation with damping ratio less than 3%.

The IROL Tv is the lower of the relay trip setting time delay, where applicable, or 30 minutes [FAC-010-2.1 R1.3, R3.6; FAC-011-2 R1.3, R3.7].   The IROL Tv may be set lower using engineering judgment, by considering factors such as, but not limited to, the risk of the event and history of equipment operation in the area.

3.7. Load Loss Threshold Guidelines

In the planning horizon and operations horizon, the value of the load loss threshold for a particular study will be six times 1% of the ERCOT Interconnection load level used in that study (6 x 1% x aggregate load level).  ERCOT ISO, the TPs, or the TOPs may deviate from this guideline as necessary but should justify the reasoning for such deviation and the deviation should maintain or improve system reliability.

The basis is that since frequency response bias used for the ERCOT Interconnection is typically set at 1% of peak load, by multiplying by a value of 6 (to represent a 0.6 Hz frequency response) results in a MW value that should result close to a 0.6 Hz frequency deviation.  In ERCOT, generator protection is set greater than 60.6 Hz, based on ERCOT regional rules.  While load of this magnitude will not typically be lost simultaneously, the guideline assumes simultaneous loss of load with no automatic frequency response which can be considered reliability margin [FAC-010-2.1 R3, R3.6; FAC-011-2 R3, R3.7].

4. Distribution of Documents and SOLs

This methodology is posted on the ERCOT ISO Market Information System (MIS) Public website.  Notifications related to revisions of the SOL Methodology for the planning horizon and operations horizon will be made prior to the effective date of the change.  When the methodology is revised, a notification of update is sent to each TOP and TP in the ERCOT Interconnection (typically through a market notice, however other equivalent means may be used).     [FAC-010-2.1 R4.2, R4.3; FAC-011-2 R4.2, R4.3].  Notification of revisions to the RC is internal to ERCOT ISO as the single PA and RC in the ERCOT Interconnection Any other PA and or RC that indicates that it has a reliability-related need for the methodology will be provided the current copy of this SOL Methodology for the Planning Horizon and Operations Horizon.   A notification of update is sent to that PA and/or RC for any future revisions, if such is requested [FAC-010-2.1 R4, R4.1, R4.2; FAC-011-2 R4, R4.1, R4.2]. If a recipient of this Methodology provides documented technical comments on the Methodology, ERCOT ISO will provide a documented response to that recipient within 45 calendar days of receipt. The response will indicate whether a change will be made to this Methodology or, if no change will be made, the reason why [FAC-010-2.1 R5; FAC-011-2 R5].

ERCOT ISO (acting as the PA) sends the assessment results annually to each NERC TOP and TP in the ERCOT Interconnection through either an e-mail distribution list or an ERCOT market notice. The results will be shared within ERCOT ISO, as appropriate. Internal communications will include the list of multiple contingencies and the associated stability limits, or notification that results did not identify any stability-related multiple contingencies [FAC-014-2 R5.3, R6.1, R6.2].

ERCOT ISO (acting as the RC) provides SOLs that ERCOT ISO has developed, including those SOLs that are identified as an IROL, to the TOPs and TPs in the ERCOT Interconnection that provide a written request that includes a schedule for delivery of those limits.  ERCOT ISO typically communicates new SOLs that are developed or modifications to existing SOLs via telemetry, an ERCOT market notice, and or the ERCOT MIS.  ERCOT ISO (acting as the RC) will also provide SOLs to any other RCs that have a reliability-related need for those limits and provide a written request that includes a schedule for delivery of those limits [FAC-014-2 R5, R5.1]. SOLs will be shared within ERCOT ISO, as appropriate, to ensure SOLs are fed back to the planning horizon as necessary [FAC-014-2 R5.1].  Any IROLs that are provided contain the information provided below [FAC-014-2 R5.1].

- Identification and status of the associated Facility (or group of Facilities) that is (are) critical to the derivation of the IROL.

- The value of the IROL and its associated Tv.

- The associated Contingency (ies).

- The type of limitation represented by the IROL (e.g., voltage collapse, angular stability).

As systems change throughout the time horizons, some or all of this information may change.  As such, the details which are not modified may not be provided an additional time, as the characteristics did not change.  For conciseness, only the elements which are modified may be communicated.  An example may be where the limit changes, but the contingencies, type of limit, and facilities that make up an interface do not change.  In such an instance, only the new limit would be provided as an update [FAC-014-2 R5.1].

It is expected TPs will provide any SOLs they have developed, in addition to the Facility rating SOLs, to ERCOT ISO and its neighboring entities as appropriate, in accordance with this methodology [FAC-014-2 R4, and R5.4].

It is expected that TOPs will provide any Facility Ratings, any special transfer limits, and any stability limits to ERCOT ISO in accordance with this methodology [FAC-014-2 R2 and R5.2].

A list of transmission Facilities that are identified to be critical to the derivation of an IROL, and the station or substation locations that are associated with the initiating contingencies leading to the identification of an IROL, will be sent to the appropriate NERC TOs and TOPs to assist those entities in identifying transmission Facilities that are Critical Assets per CIP-002-4, Attachment 1 Criterion 1.8.  Additionally, for Flexible AC Transmission Systems (FACTS) identified through analysis to be critical to the derivation of an IROL, a list of such systems and their associated contingencies will be sent to the appropriate NERC TO and TOP to assist those entities in identifying transmission Facilities that are Critical Assets per CIP-002-4, Attachment 1 Criterion 1.9.

5. Document Revisions

| Version | Description | Revision Date | Author(s) |
| --- | --- | --- | --- |
| 0 | Final Draft | 07-May-2013 | J. Chen; J. Billo; S. Solis |
| 0.1 | Minor edits to Final Draft | 23-Sept-2013 | J. Chen; J. Billo; S. Solis |
| 0.2 | Edits from comments submitted; extension of effective date to resolve Section 3.3. | 13-Sept-2013 | J. Chen; J. Billo; S. Solis |
| 0.3 | Edits from comments submitted; extension of effective date to allow for potential additional comments prior to effective date. | 24-Jan-2014 | J. Chen; J. Billo; S. Solis |

ERCOT Protocols define the Emergency Rating for the ERCOT Interconnection to be: “the two-hour MVA rating of a transmission element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature. The transmission element can operate at this rating for two hours without violation of NESC clearances or equipment failure.”

Facility Ratings in the ERCOT Interconnection include the Normal Rating, Emergency Rating, and the 15-Minute Rating.  ERCOT Protocols define the 15-minute rating to be: “The 15-minute MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature and with a step increase from a prior loading up to 90% of the Normal Rating.  The Transmission Element can operate at this rating for 15 minutes, assuming its pre-contingency loading up to 90% of the Normal Rating limit at the applicable ambient temperature, without violation of NESC clearances or equipment failure.  This rating takes advantage of the time delay associated with heating of a conductor or transformer following a sudden increase in current.”

While ERCOT ISO’s planning horizon studies start with all Facilities in service, operation horizon studies typically begin with either current or expected system topology.

Cascading is typically identified in a study when an overloaded element is removed from service, which then overloads a subsequent element, which is then removed from service for 3 consecutive iterations such that after the third iteration one or more transmission facilities remain overloaded.  An engineer may choose to not identify an SOL for a cascading event if the consequences are deemed insignificant in context of the reliability of the Interconnection. In making this determination the engineer will consider factors such as, but not limited to, if the total load loss is less than 500 MW or the total number of cascade iterations for the event.

Underfrequency load shed is set at 59.3 Hz in ERCOT; therefore, 59.4 Hz is used to determine SOLs in order to preserve a 0.1Hz margin. Generator protection is set greater than 60.6 Hz, in ERCOT; therefore, 60.4 Hz is used to determine SOLs in order to preserve a 0.2 Hz margin.

This does not include Load Resources with high set under frequency set points.