## Slide 1: Transmission Line Ground Fault Protection
Kris Koellner, LCRA TSC
ERCOT SPWG Meeting, March 17, 2014

## Slide 2: Philosophy Discussion
Would like to hear from other ERCOT TSPs regarding transmission line ground fault protection
Specifically:
  Ground time overcurrent
  Ground time instantaneous
  Ground distance

## Slide 3: Ground Time Overcurrent
Do you coordinate?
Do you periodically re-coordinate, or only for projects?
Minimum coordination interval? (e.g. 0.2 sec)
Philosophy on pickup (e.g. % line rating)
Philosophy on curve type (e.g. VI, EI, etc)
Do you use ASPEN OneLiner to automatically check?
Polarizing preference? (e.g. QV)
Options for not coordinating
  LOP torque control
  85COS torque control
  Other?

## Slide 4: Ground Time Instantaneous
Do you use it?
If so, is a certain amount of coverage required?
What is your approach for guaranteeing security over time as the system changes?
Do you check for EOL SLG fault?
How much margin is added?
Do you use ASPEN OneLiner to automatically check?
Do you disable if no coverage, or short line, or mutuals?
Do you implement a short time delay (e.g. 10 cyc)?

## Slide 5: Ground Distance
How much margin on zone 1? (e.g. max 85% or 0.1 ohm)
How much margin on zone 2? (e.g. min 120% or 0.1 ohm)
Do you consider apparent impedance in setting zone 1, 2?
Zone 2 time delay? (e.g. 20 cyc, 25 cyc, etc)
Common zone timing utilized?

## Slide 6: Bonus: Interesting event from 1/11/14
345-kV B-G fault very near Kendall substation
  Substation line arrester failed
Cleared quickly from Kendall (zone 1)
Cleared on pilot from Hays Energy (DCB scheme)
Misoperations on 138-kV line relaying at Welfare-Kendall and Boerne-Welfare

## Slide 7: Impacted Area
3
1
2
345-kV B-G fault
 ~60 miles of mutual coupling 

## Slide 8: View of fault from Kendall

## Slide 9: View of fault from Hays Energy

## Slide 10: View of fault from Welfare to Kendall LR
RBF: 247
EOLF: 1,270
50G1: 1,464 (6.10)
Model: 1,801
Event: 1,835
New: 2,335 (9.73)

## Slide 11: View of fault from Boerne to Welfare LR
RBF: 1,182
EOLF: 1,514
50G1: 1,704 (7.10)
Model: 1,801
Event: 1,815
New: 2,316 (9.65)

## Slide 12: View of fault from Antler (no trip)
RBF: 1,553
EOLF: 1,881
50G1: 2,200 (5.50)
Model: Not given
Event: 1,955
New: (same)

## Slide 13: Composition of Antler 138-kV line relay current (B phase)*
Kendall terminal closed
Kendall terminal open
Ifault
Iload
Imutual
Irelay
* Line current seen by relay =
load current + fault current + current induced by mutual coupling effects
Iload
Imutual
Irelay
Iload 84 @ 270
Imutual 659 @ -20
Ifault 597 @ 161
Irelay 128 @ 295
Iload 84 @ 270
Imutual 786 @ -17
Ifault 0 @ 0
Irelay 815 @ -23
Notes: Start with Irelay at 3 cycles (during fault, Kendall is closed)
Irelay = Iload + Ifault + Imutual
Iload is known from pre-fault data
Solve for Ifault + Imutual
Need Imutual
Use unfaulted phase to isolate Imutual since ImutualA = ImutualB = ImutualC and Ifault=0 on unfaulted phase
Once Imutual is found, solve for Ifault
Now all three vector components are known.
Now, look at Irelay at 6 cycles (during fault, Kendall is now open)
Again use unfaulted phase to isolate Imutual since ImutualA = ImutualB = ImutualC and Ifault=0 on unfaulted phase
Add Iload to Imutual on B-phase and compare vector math results to oscillography (it matches).
Draw phasor diagram to illustrate how clearing the fault leads to the misoperation.

## Slide 14: Findings
Upon clearing at Kendall, fault current re-direction caused ground fault instantaneous over-reaches at Boerne and Welfare
Event analysis at Boerne and Welfare showed that the mutual current contribution was offset by the fault current up until the Kendall terminal tripped.
After Kendall tripped, the fault current was no longer present to offset the mutual current and the relays tripped on ground instantaneous.

## Slide 15: Takeaways and corrective actions
System is well-modeled, but we did not anticipate this fault scenario.
Revising ground instantaneous standard to ensure a minimum margin of 500A, to give greater security than a 125% margin will provide at low fault duties.
  For example: 1,200  1,700 (vs. 1,500)
Reviewing the use of ground instantaneous element:
  When ground distance elements are available,
  On short lines, and
  In areas with mutual coupling.
Reaching out to other TSPs to discover best practices.

## Slide 16: Questions or Feedback?
Kris Koellner, PE
Engineering Supervisor
LCRA Transmission Services System Protection
512-578-4573
kristian.koellner@lcra.org