## Slide 1: Transmission Operator Protection System Misoperations 2013
Including Failure to Reclose
ERCOT Transmission Protections System Misoperations Data – 138kV and 345kV Combined
138kV Only
345kV Only
NOTE: Includes only transmission system protection system misoperations from 1/1/2011 thru 12/31/2013 reported by Transmission Operators

## Slide 2: Protection System Misoperations 2013
 |  | Value
# of Misoperations | Total | 198
 | 345 kV | 43
 | 138 kV | 132
 | < 100 kV | 23
By Category | Failure to Trip | 5
 | Slow Trip | 3
 | Unnecessary Trip during Fault | 89
 | Unnecessary Trip – Non Fault | 73
 | Failure to Reclose | 28
By Relay System Type | Electromechanical | 42
 | Solid State | 4
 | Microprocessor | 142
 | Other | 10
By Equipment Protected | Line | 118
 | Transformer | 21
 | Generator | 23
 | Shunt/Series Capacitor | 0
 | Shunt/Series Reactor | 5
 | Dynamic VAR system | 0
 | Bus | 13
 | Breaker | 14

## Slide 3
Summary of Human Performance Issues noted for 2013 Q4:
Generator aux transformer tripped due to ground fault detection aux CTs wired backwards.
345kV line overtrip due to modeling error. Two 345kV lines were swapped in the Aspen model.
138kV line overtrip due to incorrect directional settings. Zero sequence polarization used instead of negative sequence.
138kV line overtrip due to incorrect DC voltage jumper settings in carrier set, 250 VDC instead of 125 VDC.
Protection System Misoperations 2013

## Slide 4
Protection System Misoperation Trends (2013)

## Slide 5
Protection System Corrective Action Trends