## Slide 1: Final Report on Fast Responding Regulation Service (FRRS) Pilot Project
TAC
March 27th, 2014

## Slide 2: FRRS Pilot Overview
November 13, 2013: Board Approval
February 25, 2013: First day of Pilot
July 16, 2013: ERCOT Board approves request to extend the FRRS pilot to February 28, 2014
February 28, 2014 Pilot project ended
Three Resources participated in the pilot
      Participant 1 was a nominal 36 MW battery in Winkler/Ector County
      Participant 2 was a nominal 1 MW battery in Harris County
      Participant 3 was a nominal 0.1 MW fleet Electric Vehicle Charging Station in Tarrant County
3/27/2014
<number>
ERCOT

## Slide 3: Summary of Findings
  The introduction of FRRS improves ERCOT’s ability to arrest frequency decay during unit trips.
  FRRS Pilot Resources generally followed ERCOT FRRS deployments and responded automatically using local frequency detecting techniques.
  When deployed, FRRS reduces the rate of change of frequency and regulation deployed to conventional Resources.
  Observed lower quantities offered for FRRS-down and an overall lower performance for FRRS-down.
3/27/2014
<number>
ERCOT

## Slide 4: FRRS Performance
3/27/2014
<number>
ERCOT
FRRS Performance by Month |  | 
Month | FRRS-UP | FRRS-DN
Feb 25 - 28 2013 | 74% | 68%
March 2013 | 89% | 80%
April 2013 | 98% | 75%
May 2013 | 94% | 62%
June 2013 | 95% | 15%
July 2013 | 92% | 6%
August 2013 | 92% | No offers
September 2013 | 92% | No offers
October 2013 | 90% | No offers
November 2013 | 97% | No offers
December 2013 | 93% | No offers
January 2014 | 95% | No offers
February 2014 | 99% | No offers

## Slide 5: FRRS Performance
3/27/2014
<number>
ERCOT

## Slide 6: FRRS Performance
3/27/2014
<number>
ERCOT

## Slide 7: Detect and Respond (60 cycles) to low Frequency
3/27/2014
<number>
ERCOT

## Slide 8: Rate of Change of Frequency (RoCoF)
3/27/2014
<number>
ERCOT

## Slide 9: Rate of Change of Regulation-Up Deployments
3/26/2014
<number>
ERCOT

## Slide 10: Final Cost
3/27/2014
<number>
ERCOT
 |  | Original Payments | Final Payments | % Change
Total FRRS Payments (UP and Down) |  | $1,907,681.01 | $1,781,291.54 | -6.6%
FRRS UP | Month | Original Payments | Final Payments | % Change
 | Feb 25 - 28 2013 | $10,183.36 | $7,612.72 | -25.24%
 | March 2013 | $158,130.04 | $139,681.61 | -11.67%
 | April 2013 | $157,402.14 | $154,135.96 | -2.08%
 | May 2013 | $171,071.32 | $160,598.05 | -6.12%
 | June 2013 | $166,055.04 | $155,912.66 | -6.11%
 | July 2013 | $118,330.14 | $109,445.57 | -7.51%
 | August 2013 | $181,810.68 | $167,821.18 | -7.69%
 | September 2013 | $129,126.92 | $120,557.16 | -6.64%
 | October 2013 | $124,302.80 | $112,829.60 | -9.23%
 | November 2013 | $103,418.80 | $96,752.80 | -6.45%
 | December 2013 | $91,180.40 | $84,671.80 | -7.14%
 | January 2014 | $114,997.76 | $109,405.20 | -4.86%
 | February 2014 | $335,605.71 | $334,676.32 | -0.28%
 | Total | $1,861,615.11 | $1,754,100.63 | -5.78%

## Slide 11: Final Cost FRRS-Down
3/26/2014
<number>
ERCOT
FRRS Down | Month | Original Payments | Final Payments | % Change
 | Feb 25 - 28 2013 | $3,057.90 | $2,206.30 | -27.85%
 | March 2013 | $31,319.71 | $18,184.86 | -41.94%
 | April 2013 | $4,267.12 | $3,302.87 | -22.60%
 | May 2013 | $3,814.09 | $2,593.68 | -32.00%
 | June 2013 | $2,840.93 | $865.48 | -69.54%
 | July 2013 | $766.15 | $37.72 | -95.08%
 | August 2013 | $0.00 | $0.00 | 0.00%
 | September 2013 | $0.00 | $0.00 | 0.00%
 | October 2013 | $0.00 | $0.00 | 0.00%
 | November 2013 | $0.00 | $0.00 | 0.00%
 | December 2013 | $0.00 | $0.00 | 0.00%
 | January 2014 | $0.00 | $0.00 | 0.00%
 | February 2014 | $0.00 | $0.00 | 0.00%
 | Total | $46,065.90 | $27,190.91 | -40.97%

## Slide 12: Post Pilot
NPRR 581 became effective on Operating Day 3-1-14
  Resources can offer in and participate in Regulation and follow a Fast Responding Regulation Signal
  ERCOT continues to benefit from Resources providing FRRS
Future Ancillary Service Team (FAST) continues to work on improving Ancillary Services. (Definition of services, procurement, deployment and settlement)
3/27/2014
<number>
ERCOT