## Slide 1
NRG Comments/Concerns with Houston Import Project Assumptions
March 27, 2014 TAC Meeting

## Slide 2: Opening Remarks
The Houston Import Project (“HIP”) being recommended by ERCOT is the most expensive transmission expansion project since CREZ. The estimated cost is $590 million.
The analyses provided by ERCOT concerning HIP are extremely detailed, voluminous, and contain numerous complex scenarios and assumptions.
In spite of the breadth and complexity of the analysis, NRG and others have noticed fundamental assumptions that appear flawed, or at best highly questionable. These assumptions are driving the HIP results to a chosen end state that doesn’t solve the perceived reliability problem being addressed. In fact, the assumptions are creating the reliability problem.
The goal of this presentation is to simplify ERCOT’s large and detailed HIP analysis for TAC members by focusing on the assumptions that are driving the results.
The primary assumptions driving the results are the skewed load scaling techniques used in the analysis, combined with questionable load forecasts from the starting SSWG cases.
A TAC endorsement of this particular project, and/or the endorsement of any future project that uses similar assumptions, could lead to hundreds of millions of dollars of unnecessary transmission investments placed on the backs of consumers.

## Slide 3: Background Information Concerning the Proposed HIP Project and the Planning Assumptions
There is not enough generation to meet the SSWG Planning load in 2018, so ERCOT had to develop a methodology and assumptions to handle the problem.
ERCOT’s chosen method to solve the shortage of generation in 2018 was to scale down the load outside of Houston, mainly in the D/FW area. From ERCOT’s HIP Final Report:
  “In transmission planning analysis the amount of generation available in the base case may not be enough to meet the summed non-coincident peak load of all areas of the system. In order to solve this challenge… ERCOT split the 2018 summer peak case into two study areas, the so-called NW and SE areas. For each study area the load level was set to the forecasted peak load for that area while load outside of the area was scaled down until there was enough generation to meet the load plus an operational reserve of approximately 1375 MW.”
  “In the 2018 SE summer peak case…the load levels for the East, Coast, South Central, and Southern weather zones were set to their forecasted peak load levels. The load levels in the North, North Central, West, and Far West weather zones were reduced…from the peak load levels of the SSWG base case.”
A planning assumption of reduced load in one area of the state is electrically equivalent to adding that same amount of generation in that area.
The “SE” (Southeast) case was used in the HIP analysis. However, the NW case will also be discussed briefly during this presentation.

## Slide 4: SE Case: Weather Zones with Load Reduced Relative to 2011-2013 Peaks and Weather Zones with Load Equal to 2018 Planning Peaks
Reduced load
Reduced load
Reduced load
Reduced load
=2018 Planning peak load
=2018 Planning peak load
=2018 Planning peak load
Reduced load

## Slide 5: Load Assumptions in HIP SE Case - Quantified
SE HIP Case Loads Compared to Average Historical Weather Zone Peaks
 | Avg. Peak 2011-2013 (MWs) | 2018 SE Case Peak (MWs) | Delta MWs | Total % Change | Avg. Annual % Change 2014-2018
Zones using 2018 Peak Planning Load |  |  |  |  | 
COAST | 22,015 | 26,355 | 4,340 | 20% | 4%
SOUTH_CE | 11,573 | 14,401 | 2,828 | 24% | 5%
SOUTHERN | 5,744 | 7,103 | 1,359 | 24% | 5%
Zones with Load Reductions Relative to Avg. Peaks |  |  |  |  | 
NORTH_CE | 24,587 | 21,924 | -2,663 | -11% | -2%
NORTH | 1,996 | 1,473 | -523 | -26% | -5%
EAST | 3,642 | 3,088 | -554 | -15% | -3%
WEST | 2,411 | 1,897 | -514 | -21% | -4%
FAR_WEST | 2,819 | 2,775 | -44 | -2% | 0%

## Slide 6: What do these Assumptions Mean?
These load scaling assumptions were based on ERCOT’s “top ten” table that looked at “coincident peaks” of the other weather zones relative to the top ten Coastal peak conditions in 2011, 2012 and 2013.
The zones that have the most impact are the North Central, South and Coastal because they have significantly larger loads relative to the other weather zones.
ERCOT decreased the North Central (D/FW) load to approximately 85% of the forecasted 2018 peak load for that region, even though the above table indicates 85% is too low. A swing of 7.8% in the North Central peak load (93.37%-85.56%) equates to approximately 1,950 MWs.
Exacerbating the load scaling numbers (as discussed later) is the significant difference in the SSWG load forecasts supplied by the TSPs for the different regions. The Coastal region forecast shows tremendous peak load growth (3.6%) between now and 2018, while the North Central region’s growth is tepid at best (0.3%).
Average % of peak load of each weather zone during the top ten hourly peak load conditions at the Coast Weather Zone |  |  |  |  |  |  | 
Year | East | South | South Central | Far West | West | North | North Central
2011 | 97.46% | 98.21% | 96.38% | 93.75% | 83.70% | 67.86% | 93.37%
2012 | 96.32% | 95.58% | 96.08% | 93.23% | 92.93% | 78.55% | 85.56%
2013 | 76.77% | 98.62% | 97.42% | 95.81% | 78.23% | 90.88% | 88.81%

## Slide 7: What do these Assumptions Mean?
The data in the previous slides, coupled with the extreme differences in the SSWG load forecasts among the regions, is electrically equivalent to adding thousands of MWs of “zero-cost, must run” generation in the North Central region in 2018 while reducing the generation in the Coastal and South Regions. (As seen in the Appendix, actual interconnect activity conflicts with these assumptions.)
Since the load reductions occur at the load bus, the majority of the load reduction assumptions in the North Central region are electrically in the D/FW metroplex. The “size” of the generation added is a percentage of the peak load at the bus, and the percentage was determined by how much was needed to achieve a solvable case.
These types of assumptions undoubtedly lead to a conclusion that major transmission infrastructure is needed from the North into Houston, but the assumptions are not reasonable. This will be shown again later when discussing the “NW” case, where the assumptions are reversed.
Do we really expect negative or flat peak load growth in D/FW and between 4% and 5% annual peak load growth in the Coastal and South Central regions between now and 2018 when compared to the 2011-2013 actuals?

## Slide 8: Load Scaling Assumptions Can Only Lead to One Conclusion – Large Transfers of Power from D/FW to Houston
Loads in the Coast, SC and S weather zones were increased by 7,973 MWs in 2018 when compared to the average peaks in these zones for 2011, 2012 and 2013.
Loads in the N, NC, W, FW, and E were decreased by 3,744 MWs in 2018 when compared to the average peaks in these zones for 2011, 2012 and 2013.

## Slide 9: Comparison of Load Assumptions in ERCOT’s SE and NW case.
As an additional example of the potentially costly and unnecessary impacts of these types of load scaling assumptions, ERCOT’s 2018 “NW” case, with load scaling in the opposite direction, results in several large 345 kV upgrade projects from the Houston area towards D/FW. The load scaling assumptions in the SE and NW cases are completely contradictory to one another and could result in excessive and unnecessary costs to consumers.
Weather Zone | Avg 2011-2013 Peak | SE Case | SE Case Vs Avg 2011-2013 |  | NW Case | NW Case Vs Avg 2011-2013
COAST | 22,015 | 26,355 | 4,340 |  | 21,680 | -335
SOUTH_CE | 11,573 | 14,401 | 2,828 |  | 11,014 | -559
SOUTHERN | 5,744 | 7,103 | 1,359 |  | 5,564 | -180
Totals | 39,332 | 47,859 | 8,527 |  | 38,258 | -1,074
FAR_WEST | 2,819 | 2,775 | -44 |  | 3,176 | 357
NORTH | 1,996 | 1,473 | -523 |  | 1,747 | -249
EAST | 3,642 | 3,088 | -554 |  | 2,242 | -1,400
NORTH_CE | 24,587 | 21,924 | -2,663 |  | 29,512 | 4,925
WEST | 2,411 | 1,897 | -514 |  | 2,230 | -181
Totals | 35,455 | 31,157 | -4,298 |  | 38,907 | 3,452
SE and NW HIP Case Loads Compared to Average Historical Weather Zone Peaks
Note: The NW case shows total loading on some of the SE case “overloaded” North to Houston lines of less than 300 MWs. Both cases can’t be right.

## Slide 10: Residential Transmission Charges for Oncor and CNP
Transmission System Charges are the sum of the distribution tariff Transmission Charge and the Transmission Cost Recovery Factor
CNP is up 127% from 2003
Oncor is up 146% from 2003
2014 transmission costs will be even higher as all of CREZ costs are captured in the TCRF

## Slide 11: Questions for Consideration
Why does the 2018 SSWG case indicate a 4-5% average annual load growth (when compared to average annual 2011-2013 peaks) in the Coastal and South Central zones, while the North Central zone shows around 0.3% growth?
If a planning case cannot be solved because there is not enough generation, shouldn’t the load be scaled somewhat proportionally throughout ERCOT, rather than in one particular region?
Is it proper to completely reverse the load scaling assumptions when studying 2 different regions in ERCOT, i.e., the SE and NW cases? Won’t this always result in large import/export projects between regions, but with load flows being significantly different in the 2 cases?
Should planning cases follow generation addition assumptions word for word from the protocols and planning guides (air permit, water, financial security, etc.), yet use skewed regional load assumptions that have the same electrical impact as either adding or removing generation?
Should there be vastly different load growth assumptions in the CDR vs. the transmission planning cases? Should Pondera King be included in 2018 CDR but not in transmission planning scenarios?
For any type of transmission import and/or export expansion project to work, doesn’t there have to be generation to import or export?

## Slide 12: Conclusions
With the load reduction assumptions used in the HIP analysis (combined with the vastly different SSWG load growth assumptions used to start the HIP analysis), the only way the project solves anything is if no generation is built in the South or Coastal region, but thousands of MWs are built in the North Central region (primarily D/FW area) before 2018. [Note: See the Appendix for additional information on publicly available generation new builds. The data indicates more generation FIS activity in the Coastal and Southern regions than in the North Central region, which is in direct conflict with the HIP load reduction assumptions .]
The load reduction assumptions used to make the analysis “solvable” are unrealistic when compared to reality.
Building a major transmission corridor with nothing to import could lead to stranded, costly transmission investments placed on the backs of consumers.
More logical, realistic assumptions for the load scenarios in the HIP analysis across the regions would provide a vastly different result and a more cost-effective utilization of consumer dollars.

## Slide 13
APPENDIX

## Slide 14: ERCOT’s “Sensitivity” Analysis
Based on concerns from NRG and others on the load scaling methodology used in the HIP analysis, ERCOT ran several sensitivity analyses. The sensitivity cases are described on page 8 and in Appendix E of ERCOT’s HIP Final Report.
A closer look at the 3 sensitivity cases in Appendix E shows similar issues with the load assumptions as described previously.
For example, in all 3 Sensitivity Cases, the 2018 peak loads in the North Central weather zone are lower than the Coastal zone peaks. Peak load in the North Central Zone has historically been higher than the Coastal zone.
When compared to the average annual weather zone peaks in 2011-2013, the 2018 peak loads shown in Sensitivity Case # 1 (SSWG case) show an average annual growth of 3.6% to 4.6% in the Coastal and South Central zones and only a 0.3% average annual growth in the North Central zone.
And Sensitivity Cases #2 and #3 actually have “negative” load growth in the North Central zone when compared to the average annual 2011-2013 peaks.
Because of these load discrepancies (and the 50% wind output used in SSWG case), ERCOT’s Appendix E Sensitivity analysis finds overloads or heavy flows on the 345 kV lines between D/FW and Houston. However, more consistent and believable load assumptions would have vastly changed the line loadings.

## Slide 15: ERCOT’s Sensitivity Case 1 Comparison of Load Growth Assumptions for 2018
Table 4: Sensitivity Case 1, 2018 MW load assumptions used in the HIP analysis compared to the average weather zone peaks for 2011-2013.
 | Avg. Peak 2011-2013 (MWs) | 2018 SSWG Case 1 Peaks (MWs) | Delta MWs | Total % Change | Avg. Annual % Change 2014-2018
COAST | 22,015 | 25,937 | 3,922 | 18% | 3.6%
SOUTH_CE | 11,573 | 14,241 | 2,668 | 23% | 4.6%
SOUTHERN | 5,744 | 6,564 | 820 | 14% | 2.9%
NORTH_CE | 24,587 | 24,950 | 363 | 1% | 0.3%
NORTH | 1,996 | 1,858 | -138 | -7% | -1.4%
EAST | 3,642 | 2,554 | -1,088 | -30% | -6.0%
WEST | 2,411 | 2,334 | -77 | -3% | -0.6%
FAR_WEST | 2,819 | 3,429 | 610 | 22% | 4.3%
Note: Sensitivity Cases #2 and #3 actually show “negative” load growth by 2018 in the North Central weather zone when compared to the 2011-2013 average annual peaks, while the Coastal and South Central weather zones have strong load growth assumptions between the 2011-2013 averages and 2018.

## Slide 16: ERCOT’s SGIA Data Doesn’t Support the Load Reduction Assumptions
Source: ERCOT System Planning Monthly Status Report – December, 2013, Renewables Removed.
Total by Region | MW | %
Coastal | 2340 | 31.4
West | 570 | 7.6
North | 1079 | 14.5
North Central | 3226 | 43.3
Far West | 240 | 3.2
Total | 7455 | 100
Table 7: IAs by Region
Generation Interconnection Agreements as of December 31, 2013 |  |  |  |  |  |  | 
INR | Site Name | County | COD | Fuel | MW For Grid | Change from Last Report | Zone
14INR0016 | Channel Energy Center 138/345kV CT | Harris | 14-Jun | Gas | 190 |  | Coastal
14INR0015 | Deer Park Energy Center | Harris | 14-Jul | Gas | 190 | MW for Grid | Coastal
13INR0021 | Ferguson Replacement Project | Llano | 14-Jul | Gas | 570 |  | West
13INR0040 | Rentech Project | Harris | 14-Aug | Gas | 15 |  | Coastal
10INR0021 | Panda Sherman Power | Grayson | 14-Aug | Gas | 720 |  | North
10INR0020a | Panda Temple Power | Bell | 14-Aug | Gas | 717 |  | North Central
10INR0020b | Panda Temple Power | Bell | 15-Aug | Gas | 717 |  | North Central
13INR0049 | Friendswood Energy Generation | Harris | 15-Sep | Gas | 316 |  | Coastal
13INR0023 | Texas Clean Energy Project | Ector | 16-Jan | Coal | 240 |  | Far West
13INR0028 | Antelope Station | Hale | 16-Jun | Gas | 359 |  | North
06INR0006 | Cobisa-Greenville | Hunt | 16-Dec | Gas | 1792 | Projected COD | North Central
10INR0022 | Pondera King Power Project | Harris | 16-Dec | Gas | 1629 | MW for Grid,Proj. COD | Coastal

## Slide 17: ERCOT’s Full Interconnect Study Data Doesn’t Support the Load Reduction Assumptions
Source: ERCOT System Planning Monthly Status Report – December, 2013, Renewables Removed.
1.1 Generation Projects Undergoing Full Interconnection Studies |  |  |  |  | 
Interconnection Database Reference Number | County | Fuel | Capacity to Grid (MW) | Commercial Operation (from resource developer) | Zone
14INR0069 | Milam | Coal | 30 | 14-Mar | South Central
14INR0040 | Hidalgo | Gas | 225 | 14-Jun | South
14INR0059 | Kaufman | Gas | 52 | 14-Aug | North Central
14INR0066 | Lamar | Gas | 130 | 14-Nov | North
13INR0054 | Bee | Gas | 25 | 14-Dec | South
14INR0039 | Ector | Gas | 450 | 15-Mar | Far West
14INR0038 | Galveston | Gas | 390 | 15-Apr | Coastal
15INR0053 | Winkler | Gas | 123 | 15-May | Far West
15INR0054 | Reeves | Gas | 123 | 15-May | Far West
15INR0055 | Austin | Gas | 142 | 15-May | South Central
15INR0027 | Hidalgo | Gas | 79 | 15-Jun | South
15INR0028 | Freestone | Gas | 160 | 15-Jun | East
15INR0042 | Hood | Gas | 460 | 15-Jun | North Central

## Slide 18: ERCOT’s Full Interconnect Study (“FIS”) Data Doesn’t Support the Load Reduction Assumptions, Cont.
Source: ERCOT System Planning Monthly Status Report – December, 2013, Renewables Removed.
1.1 Generation Projects Undergoing Full Interconnection Studies |  |  |  |  | 
Interconnection Database Reference Number | County | Fuel | Capacity to Grid (MW) | Commercial Operation (from resource developer) | Zone
15INR0023 | Wharton | Gas | 700 | 15-Jun | Coastal
16INR0010 | Mitchell | Gas | 799 | 16-Feb | West
16INR0009 | Calhoun | Gas | 510 | 16-Apr | Coastal
16INR0006 | Angelina | Gas | 785 | 16-Jun | East
16INR0003 | Brazoria | Gas | 11 | 16-Jun | Coastal
16INR0004 | Cameron | Gas | 730 | 16-Jun | South
16INR0005 | Cameron | Gas | 871 | 16-Jun | South
16INR0007 | Hidalgo | Gas | 95 | 16-Jun | South
17INR0004 | Hale | Gas | 202 | 16-Jun | North
15INR0032 | Hale | Gas | 197 | 16-Jul | North
15INR0033 | Hale | Gas | 197 | 16-Jul | North
16INR0013 | Nacogdoches | Gas | 215 | 16-Jul | East
17INR0002 | Henderson | Gas | 489 | 17-Jun | North Central
17INR0003 | Jackson | Gas | 965 | 17-Jun | Coastal
17INR0007 | Wharton | Gas | 1177 | 17-Jul | Coastal
11INR0040 | Freestone | Gas | 640 | 18-Mar | East
Total by Region | MW | % | C + S + SC + E | W + N + NC + FW
Coastal | 3753 | 34.2 | 3753 | 
West | 799 | 7.3 |  | 799
North | 726 | 6.6 |  | 726
North Central | 1001 | 9.1 |  | 1001
Far West | 696 | 6.3 |  | 696
South | 2025 | 18.5 | 2025 | 
South Central | 172 | 1.6 | 172 | 
East | 1800 | 16.4 | 1800 | 
Total | 10972 | 100 | 7,750 | 3,222
There is over twice as much generation under FIS in the Coastal, South Central, South and East weather zones than in the North Central, West, North and Far West weather zones. This is in direct contradiction to the “load reduction” assumptions used in the HIP analysis.