## Slide 1
Houston Import Project Observations for the Technical Advisory Committee’s Consideration
TAC Meeting
March 27th, 2014
Notes: <number>

## Slide 2: Overview
Calpine asks the Technical Advisory Committee to consider two significant issues that have recently surfaced relative to the Houston Import Project:
Several load buses in the 2018 SSWG’s Base Case show very large percentage changes from the 2014 peak loads for those buses; percentage changes that are unlikely to be residential or commercial development and are likely industrial development requiring cogeneration development not accounted for in the HIP studies,
ERCOT’s latest CDR shows the Pondera King Power Project’s capacity available for 2018 yet it is not considered in the HIP studies.
<number>

## Slide 3: Possible Cogen Load Locations in Houston (SSWG 2018 vs. 2014)
<number>
Alvin-Texas City
89MW 76%
Mt. Belvieu
210MW
86%
Springwoods
74MW 63%
(after discount load roll-over)
EXXON
37MW
39%
Houston
MOORE
14MW(new)
Notes: 2014 to 2018 load growth by MW and by % at each load pocket.
<number>

## Slide 4: Bus List of Possible Cogen from SSWG 2018 vs. 2014
<number>
Bus # | Bus Name | 2018 Load (MW) | 2014 Load (MW) | 18 vs. 14 change | % changed | Region
38920 | TNLEAGCITY1 | 123 | 101 | 22 | 22% | Alvin-Texas City
38990 | TNSEMINOLE1 | 45 | 31 | 14 | 46% | Alvin-Texas City
38900 | TNHDNLAKES1 | 22 | 0 | 22 |  | Alvin-Texas City
38930 | TNUTMB____1 | 20 | 0 | 20 |  | Alvin-Texas City
38830 | TNMAINLAND1 | 11 | 0 | 11 |  | Alvin-Texas City
39015 | TNNALVIN__1 | 11 | 0 | 11 |  | Alvin-Texas City
40570 | EXXON___138A | 131 | 94 | 37 | 39% | EXXON
40555 | MOORE___138X | 14 | 0 | 14 |  | MOORE
40665 | CONNOR__138X | 25 | 1 | 24 | 2370% | Mt. Belvieu
41611 | TRNITY__138B | 32 | 8 | 24 | 281% | Mt. Belvieu
40764 | WINFRE__138X | 53 | 30 | 23 | 78% | Mt. Belvieu
41111 | MT_BEL__138A | 129 | 95 | 34 | 36% | Mt. Belvieu
40760 | NORTON_138X | 77 | 51 | 26 | 50% | Mt. Belvieu
40770 | HACHER__138X | 80 | 47 | 33.00 | 71% | Mt. Belvieu
41610 | TRINTY__138A | 61 | 14 | 47.00 | 338% | Mt. Belvieu
46270 | SPRINGWOODS | 212 | 130 | 82 | 64% | Springwoods
Total |  | 1046 | 602 | 444 | 74% | 
Notes: <number>

## Slide 5: Possible Cogen Load Locations in South WZ (SSWG 2018 vs. 2014)
<number>
ETP/Tenaris
76MW
135%
Tuleta/ McCampbell
76MW(new)
Notes: 2014 to 2018 load growth by MW and by % at each load pocket.
<number>

## Slide 6: Bus List of Possible Cogen in South WZ (SSWG 2018 vs. 2014)
<number>
Bus # | Bus Name | 2018 Load (MW) | 2014 Load (MW) | 18 vs. 14 change | % changed | Region
5523 | ETPSUB8 | 98 | 56 | 42 | 43% | ETP/Tenaris
5562 | TENARISSUB8 | 34 | 0 | 34 |  | ETP/Tenaris
8590 | TULETA4EA | 38 | 0 | 38 |  | Tuleta/ McCampbell
80470 | MCCAMPB4 | 38 | 0 | 38 |  | Tuleta/ McCampbell
Total |  | 208 | 56 | 152 | 271% | 
Notes: <number>

## Slide 7: Pondera King Power Project
<number>
SITE_NAME | GINR_NUM | UNIT_CODE | COUNTY | FUEL | ZONE | YEAR | 2014 | 2015 | 2016 | 2017 | 2018
New Resources with Signed IA and Air Permit |  |  |  |  |  |  |  |  |  |  | 
PANDA SHERMAN CTG1 | 10INR0021 | PANDA_S_SHER1CT1 | GRAYSON | GAS | NORTH | 2014 | - | 192.8 | 192.8 | 192.8 | 192.8
PANDA SHERMAN CTG2 | 10INR0021 | PANDA_S_SHER1CT2 | GRAYSON | GAS | NORTH | 2014 | - | 192.8 | 192.8 | 192.8 | 192.8
PANDA SHERMAN STG | 10INR0021 | PANDA_S_SHER1ST1 | GRAYSON | GAS | NORTH | 2014 | - | 334.7 | 334.7 | 334.7 | 334.7
PANDA TEMPLE CTG1 | 10INR0020a | PANDA_T1_TMPL1CT1 | BELL | GAS | NORTH | 2014 | - | 191.2 | 191.2 | 191.2 | 191.2
PANDA TEMPLE CTG2 | 10INR0020a | PANDA_T1_TMPL1CT2 | BELL | GAS | NORTH | 2014 | - | 191.2 | 191.2 | 191.2 | 191.2
PANDA TEMPLE STG | 10INR0020a | PANDA_T1_TMPL1ST1 | BELL | GAS | NORTH | 2014 | - | 334.7 | 334.7 | 334.7 | 334.7
DEER PARK ENERGY CENTER | 14INR0015 | DDPEC_GT6 | HARRIS | GAS | HOUSTON | 2014 | - | 165.0 | 165.0 | 165.0 | 165.0
FERGUSON REPLACEMENT CTG1 | 13INR0021 | FERGCC_FERGGT1 | LLANO | GAS | SOUTH | 2014 | - | 161.9 | 161.9 | 161.9 | 161.9
FERGUSON REPLACEMENT CTG2 | 13INR0021 | FERGCC_FERGGT2 | LLANO | GAS | SOUTH | 2014 | - | 161.9 | 161.9 | 161.9 | 161.9
FERGUSON REPLACEMENT STG | 13INR0021 | FERGCC_FERGST1 | LLANO | GAS | SOUTH | 2014 | - | 186.0 | 186.0 | 186.0 | 186.0
TEXAS CLEAN ENERGY PROJECT | 13INR0023 |  | ECTOR | COAL | WEST | 2018 | - | - | - | - | -
PANDA TEMPLE II | 10INR0020b |  | BELL | GAS | NORTH | 2015 | - | - | 717.0 | 717.0 | 717.0
PONDERA KING POWER PROJECT | 10INR0022 |  | HARRIS | GAS | HOUSTON | 2018 | - | - | - | - | 1,468.6
From the Winter 2014 CDR
From the ERCOT Planning Update to the RPG on 1/21/2014

## Slide 8: Our Conclusions
<number>
If you believe that the bus load growths we’ve identified are likely industrial development and will require power and/or steam, then you should also believe that they will be supplied locally and not from the North Central Weather Zone. New cogeneration development in the Houston Area will be needed to match these loads yet no such assumption was used in the HIP studies.
It may be useful to exclude the Pondera King Power Project from the HIP studies in order to support an apparent need for new North-Houston transmission, and it may also appropriate to include that same facility in the CDR for resource adequacy purposes but doing both raises an obvious question about the discontinuity between resource adequacy planning and transmission planning.

## Slide 9
Notes: <number>