| NOGRR Number | 124 | NOGRR Title | Additional VRT Requirements for IRRs |
| --- | --- | --- | --- |

| Date | March 31, 2014 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | M. Wagner on behalf of Edison Mission Marketing & Trading |
| E-mail Address | mwagner@edisonmission.com |
| Company | Edison Mission Marketing & Trading |
| Phone Number |  |
| Cell Numbers | 617-529-3127 |
| Market Segment | Independent Generator |

Comments

Edison Mission Marketing & Trading (EMMT) supports the technical analysis conducted by ERCOT to move this issue forward, and we appreciate the dialogue and interaction ERCOT has conducted with stakeholders in this regard. However, as we have expressed at various meetings on this Nodal Operating Guide Revision Request (NOGRR), we continue to oppose the retroactive nature of this proposal—not the technical requirements themselves-- and that is the nature of the comments herein.

ERCOT’s proposed effective date in this NOGRR, August  30, 2013, is also the NOGRR submission  date.  Thus, ERCOT proposes to have a standard be effective on the same day it was introduced to stakeholders. Clearly it is unreasonable to expect a generation investor to support a process wherein a standard is proposed and effective on the same date. Thus, we recommend this NOGRR become effective on the first of the month following NOGRR approval.

Below we modify OWG’s language of March 19, 2014 to change the reference date to the first of the month following the date of approval of the NOGRR. We appreciate the opportunity to work with ERCOT and Stakeholders on this important issue.

Revised Cover Page Language

None.

Revised Proposed Guide Language

2.9.1	Additional Voltage Ride-Through Requirements for Intermittent Renewable Resources

(1)	All Intermittent Renewable Resources (IRRs) shall also comply with the requirements of this Section, except as follows:

(a)	An IRR that  interconnects to  the ERCOT System pursuant to a Standard Generation Interconnection Agreement (SGIA) (i) executed on or before [insert date that is first month following date of NOGRR Approval] and (ii) under which the IRR provided all required financial security to the TSP on or before  insert date that is first of month following date of NOGRR Approval], is not required to meet any high VRT requirement greater than 1.1 per unit voltage unless the interconnected IRR includes one or more turbines that differ from the turbine model(s) described in the SGIA (including any attachment thereto), as that agreement existed on [insert date that is first of month following date of NOGRR Approval].  Notwithstanding the foregoing, if the Resource Entity that owns or operates an IRR that was interconnected pursuant to an SGIA executed before [insert date that is first of month following date of NOGRR Approval], under which the IRR provided all required financial security to the TSP on or before [insert date that is first of month following date of NOGRR], demonstrates to ERCOT’s satisfaction that the high VRT capability of the IRR is not lower than the capability of the turbine model(s) described in the SGIA (including any attachment thereto), as that agreement existed on Jinsert date that is first of month following date of NOGRR] that IRR is not required to meet the high VRT requirement in this Section.

(b)	An IRR that interconnects to the ERCOT System pursuant to an SGIA executed prior to November 1, 2008 is not required to meet VRT requirements presented in this Section.  However, any WGR that is installed on or after November 1, 2008 and that initially synchronizes with the ERCOT System, pursuant to a Standard Generation Interconnection Agreement (SGIA) (i) executed on or before [insert date that is first of the month following date of NOGRR Approval], and (ii) under which the IRR provided all required financial security to the TSP on or before [insert date that is first of month following date of NOGRR Approval (except for an IRR installed pursuant to an SGIA executed before November 1, 2008) shall be VRT-capable in accordance with the low VRT requirements in this Section and high-voltage requirements in this Section up to 1.1 per unit voltage unless the interconnected IRR includes one or more turbines that differ from the turbine model(s) described in the SGIA (including any attachment thereto), as that agreement existed on [insert date that is first of month following date of NOGRR Approval] in which case the IRR shall also be required to comply with the high VRT requirements of this section, subject to the exemption described in paragraph (a), above..

(c)	An IRR that is not technically capable of complying with a 1.2 per unit voltage high VRT requirement and that is not subject to either of the exemptions described in paragraphs (a) or (b), above, is not required to meet any high Voltage Ride-Through (VRT) requirement greater than 1.1 per unit voltage until [insert date that is first of month following date of NOGRR Approval] 2016.

(d)	Notwithstanding any of the foregoing provisions, an IRR’s VRT capability shall not be reduced over time.

(2	)	Each IRR shall provide technical documentation of VRT capability to ERCOT upon request.

(3)	Each IRR is required to set generator voltage relays to remain in service for at least 0.15 seconds during all transmission faults and to allow the system to recover as illustrated in Figure 1, Default Voltage Ride-Through Boundaries for IRRs, below.  Recovery time to 90% of per unit voltage should be within 1.75 seconds.  Faults on individual phases with delayed clearing (zone 2) may result in phase voltages outside this boundary but if the phase voltages remain inside this boundary, then generator voltage relays are required to be set to remain connected and recover as illustrated in Figure 1.

(4)	Each IRR shall remain interconnected during three-phase faults on the ERCOT System for a voltage level as low as zero volts with a duration of 0.15 seconds as measured at the Point of Interconnection (POI) unless a shorter clearing time requirement for a three-phase fault specific to the generating plant POI is determined by and documented by the TSP in conjunction with the SGIA.  The clearing time requirement shall not exceed nine cycles.

(5)	Each IRR shall set generator voltage relays to remain interconnected to the ERCOT System during the following high-voltage conditions, as illustrated in Figure 1: any per-unit voltage equal to or greater than 1.175 but less than 1.2 for up to 0.2 seconds, any per-unit voltage equal to or greater than 1.15 but less than 1.175 per unit voltage for up to 0.5 seconds, and any per-unit voltage equal to or greater than 1.1 but less than 1.15 for up to 1.0 seconds.  The indicated voltages are measured at the POI.

(6)	An IRR may be tripped Off-Line after the fault clearing period if this action is part of an approved Special Protection Systems (SPSs).

(7)	VRT requirements may be met by the performance of the generators; by installing additional reactive equipment behind the POI; or by a combination of generator performance and additional equipment behind the POI.  VRT requirements may be met by equipment outside the POI if documented in the SGIA.

(8)	If an IRR fails to comply with the clearing time or recovery VRT requirement, then the IRR and the interconnecting TSP shall be required to investigate and report to ERCOT on the cause of the IRR trip, identifying a reasonable mitigation plan and timeline.

Figure 1:  Default Voltage Ride-Through Boundaries for IRRs.

From various public discussion/documents, it appears that the grandfather date of 8/30/13 was derived by evaluating a desired transfer limit from the panhandle and backing into a workable number of grandfathered MW. The seemingly fluid nature of the date choice of August 30, 2013, is evidenced by ERCOT’s willingness to consider a later effective date (January 2014), proposed by another market participant in February 2014. (See comments from EDF-RE filed 2/12/14.)  We support ERCOT’s move to a more current date and believe that this proposed standard and all other new standards should apply at a defined point subsequent to approval of the standard.