| NOGRR Number | 124 | NOGRR Title | Additional VRT Requirements for IRRs |
| --- | --- | --- | --- |

| Date | April 1, 2014 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Jason Minalga on behalf of Invenergy Energy Management, LLC |
| E-mail Address | jminalga@invenergyllc.com |
| Company | Invenergy Energy Management, LLC |
| Phone Number | 312-582-1500 |
| Cell Number | 630-803-3605 |
| Market Segment | Independent Generator |

Comments

Invenergy is generally supportive of ERCOT’s efforts to address reliability concerns in the Panhandle region. Invenergy would support the requirement as proposed by ERCOT on January 26, 2014 so long as it does not:

- Harm projects that are in late stage development—under construction, commercially online, have executed financial hedge agreements, or procured substantial equipment, which would cause an unreasonable amount of additional cost to change out equipment. We are concerned of the retroactive nature of this requirement and would encourage ERCOT to ensure this does not happen.

- Allow for exception to NOGRR124 in excess of what the system can reliably accommodate. ERCOT should be flexible in managing exceptions to prevent harm to late-stage projects while managing Panhandle-area reliability. We are concerned that allowing excessive megawatts of projects to be excepted from NOGRR124 requirements could cause additional long-term issues for projects that are operating or that have complied with NOGRR124 and could be harmed by projects that have not complied or are not required to comply.

Invenergy would encourage projects that can comply with a reasonable amount of additional expense to make every effort to do so. This would provide greater certainty to ERCOT on maintaining reliability, reduce risk to projects that have complied or that are operating, and may allow ERCOT to except additional projects that may have significant additional costs to comply with the requirement.

Invenergy would also ask that a more standardized process be developed to detail the procedure, study assumptions, etc. for addressing NOGRR124 compliance during the interconnection study process. We have provided language for consideration to satisfy this request.

Revised Cover Page Language

None.

Revised Proposed Guide Language

2.9.1	Additional Voltage Ride-Through Requirements for Intermittent Renewable Resources

(1)	All Intermittent Renewable Resources (IRRs) shall also comply with the requirements of this Section, except as follows:

(a)	An IRR that  interconnects to  the ERCOT System pursuant to a Standard Generation Interconnection Agreement (SGIA) (i) executed on or before January 16, 2014and (ii) under which the IRR provided all required financial security to the TSP on or before January 16, 2014, is not required to meet any high VRT requirement greater than 1.1 per unit voltage unless the interconnected IRR includes one or more turbines that differ from the turbine model(s) described in the SGIA (including any attachment thereto), as that agreement existed on January 16, 2014.  Notwithstanding the foregoing, if the Resource Entity that owns or operates an IRR that was interconnected pursuant to an SGIA executed before January 16, 2014, under which the IRR provided all required financial security to the TSP on or before January 16, 2014, demonstrates to ERCOT’s satisfaction that the high VRT capability of the IRR is not lower than the capability of the turbine model(s) described in the SGIA (including any attachment thereto), as that agreement existed on January 16, 2014 that IRR is not required to meet the high VRT requirement in this Section.

(b)	An IRR that interconnects to the ERCOT System pursuant to an SGIA executed prior to November 1, 2008 is not required to meet VRT requirements presented in this Section.  However, any WGR that is installed on or after November 1, 2008 and that initially synchronizes with the ERCOT System, pursuant to a Standard Generation Interconnection Agreement (SGIA) (i) executed on or before January 16, 2014, and (ii) under which the IRR provided all required financial security to the TSP on or before January 16, 2014(except for an IRR installed pursuant to an SGIA executed before November 1, 2008) shall be VRT-capable in accordance with the low VRT requirements in this Section and high-voltage requirements in this Section up to 1.1 per unit voltage unless the interconnected IRR includes one or more turbines that differ from the turbine model(s) described in the SGIA (including any attachment thereto), as that agreement existed on January 16, 2014 in which case the IRR shall also be required to comply with the high VRT requirements of this section, subject to the exemption described in paragraph (a), above..

(c)	An IRR that is not technically capable of complying with a 1.2 per unit voltage high VRT requirement and that is not subject to either of the exemptions described in paragraphs (a) or (b), above, is not required to meet any high Voltage Ride-Through (VRT) requirement greater than 1.1 per unit voltage until January 16, 2016

(d)	Notwithstanding any of the foregoing provisions, an IRR’s VRT capability shall not be reduced over time.

(e) 	The design of the High Voltage Ride Through (HVRT) capability for after post-event transients above 1.1 per unit voltage at the POI shall not be required for pre-event initial conditions of less than 1.0 per unit voltage at the POI.  The design for HVRT capability of transients up to 1.2 per unit voltage shall be verified for the following initial condition: WGR output power at 100% of design capability, voltage at the POI equal to 1.0 per unit and WGR reactive output equal to zero.

(2	)	Each IRR shall provide technical documentation of VRT capability to ERCOT upon request.

(3)	Each IRR is required to set generator voltage relays to remain in service for at least 0.15 seconds during all transmission faults and to allow the system to recover as illustrated in Figure 1, Default Voltage Ride-Through Boundaries for IRRs, below.  Recovery time to 90% of per unit voltage should be within 1.75 seconds.  Faults on individual phases with delayed clearing (zone 2) may result in phase voltages outside this boundary but if the phase voltages remain inside this boundary, then generator voltage relays are required to be set to remain connected and recover as illustrated in Figure 1.

(4)	Each IRR shall remain interconnected during three-phase faults on the ERCOT System for a voltage level as low as zero volts with a duration of 0.15 seconds as measured at the Point of Interconnection (POI) unless a shorter clearing time requirement for a three-phase fault specific to the generating plant POI is determined by and documented by the TSP in conjunction with the SGIA.  The clearing time requirement shall not exceed nine cycles.

(5)	Each IRR shall set generator voltage relays to remain interconnected to the ERCOT System during the following high-voltage conditions, as illustrated in Figure 1: any per-unit voltage equal to or greater than 1.175 but less than 1.2 for up to 0.2 seconds, any per-unit voltage equal to or greater than 1.15 but less than 1.175 per unit voltage for up to 0.5 seconds, and any per-unit voltage equal to or greater than 1.1 but less than 1.15 for up to 1.0 seconds.  The indicated voltages are measured at the POI.

(6)	An IRR may be tripped Off-Line after the fault clearing period if this action is part of an approved Special Protection Systems (SPSs).

(7)	VRT requirements may be met by the performance of the generators; by installing additional reactive equipment behind the POI; or by a combination of generator performance and additional equipment behind the POI.  VRT requirements may be met by equipment outside the POI if documented in the SGIA.

(8)	If an IRR fails to comply with the clearing time or recovery VRT requirement, then the IRR and the interconnecting TSP shall be required to investigate and report to ERCOT on the cause of the IRR trip, identifying a reasonable mitigation plan and timeline.

Figure 1:  Default Voltage Ride-Through Boundaries for IRRs.