| NOGRR Number | 124 | NOGRR Title | Additional VRT Requirement for IRRs |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Recommended Approval |
| Date of Decision |  | April 3, 2014 |  |  |
| Proposed Effective Date |  | May 1, 2014 |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Operating Guide Section Requiring Revision |  | 2.9.1, Additional Voltage Ride-Through Requirements for Intermittent Renewable Resources |  |  |
| Protocol Section(s) Requiring Revision |  | None. |  |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) specifies new high Voltage Ride-Through (VRT) requirements for Intermittent Renewable Resources (IRRs). |  |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) To maintain system reliability by establishing additional VRT requirements for IRRs. |  |  |
| Procedural History |  | - On 8/30/13, NOGRR124 and an Impact Analysis were posted. - On 9/18/13, the Operations Working Group (OWG) considered NOGRR124. - On 10/16/13, ERCOT comments were posted. - On 10/16/13, OWG again considered NOGRR124. - On 12/17/13, OWG considered the 10/16/13 OWG Report and Impact Analysis for NOGRR124. - On 1/26/14, ERCOT comments were posted. - On 1/27/14, OWG considered the 12/17/13 OWG Report and Impact Analysis for NOGRR124. - On 2/12/14, EDF-RE comments were posted. - On 3/19/14, OWG considered the 1/27/14 OWG Report and Impact Analysis for NOGRR124. - On 3/31/14, Edison Mission Marketing & Trading comments were posted. - On 4/1/14, Invenergy comments were posted. - On 4/2/14, ERCOT comments were posted. - On 4/3/14, ROS considered the 3/19/14 OWG Report for NOGRR124. |  |  |
| OWG Decision |  | On 9/18/13, OWG was in consensus to table NOGRR124 until the next OWG meeting. On 10/16/13, OWG was in consensus to recommend approval of NOGRR124 as amended by the 10/16/13 ERCOT comments. On 12/17/13, OWG was in consensus to table NOGRR124 for one month. On 1/27/14, OWG was in consensus to table NOGRR124. On 3/19/14, OWG was in consensus to recommend approval of NOGRR124 as amended by 2/12/14 EDF-RE comments and as revised by OWG, with the exception of endorsing any particular grandfathering date. |  |  |
| Summary of OWG Discussion |  | On 9/18/13, Market Participants discussed the pros and cons of a potential requirement for incremental improvement of voltage-related equipment versus the concept of “whole-farm replacement,” and the need for additional OWG consideration of these and related issues. On 10/16/13, participants reviewed the 10/16/13 ERCOT comments and proposed edits to the Revision Description. On 12/17/13, participants concluded that a workshop is necessary to address additional concerns with NOGRR124 and that one will be scheduled for January 2014. On 1/27/14, participants reviewed the 1/26/14 ERCOT comments and requested that additional time be allowed for their consideration. On 3/19/14, participants discussed the 2/12/14 EDF-RE comments. Some participants were opposed to the date recommended in the EDF-RE comments for application of the new VRT requirements to projects already under development as it would be unduly burdensome for these projects to obtain additional funding to cover the costs of compliance with NOGRR124. Other participants objected generally to the concept of retroactive application of new requirements to projects in development prior to TAC approval of NOGRR124. |  |  |
| ROS Decision |  | On 4/3/14, ROS voted to recommend approval of NOGRR124 as recommended by OWG in the 3/19/14 OWG Report, but notes that ROS expresses disappointment with the retroactivity of NOGRR124. There was one abstention from the Cooperative Market Segment. All Market Segments were present for the vote. |  |  |
| Summary of ROS Discussion |  | On 4/3/14, participants discussed the 3/31/14 EMMT and 4/1/14 Invenergy comments to NOGRR124. Participants discussed the date for application of new VRT requirements, proposed in NOGRR124, to projects already under development. ERCOT Staff noted that the greater the number of MWs that are not subject to NOGR124, the greater the chance for curtailment of those same Resources, particularly in the Texas Panhandle area. A motion to recommend approval of NOGRR124 as amended by the 3/31/14 EMMT comments failed. |  |  |

| Business Case |  |
| --- | --- |
| 1 | The stability analysis in the ERCOT Panhandle Renewable Energy Zone study indicates a potential cascading wind generation trip due to overvoltage during and post contingency period and can lead to voltage collapse in the Panhandle area if a large amount of wind generation projects in the Panhandle area do not have adequate high VRT capability. These problems may develop in other areas where the concentration of IRRs could increase. |
| 2 | This NOGRR will help to maintain system reliability by preventing IRRs from tripping during and after contingencies that are less severe than the defined thresholds and that occur for certain limited durations. |

| Sponsor |  |
| --- | --- |
| Name | Jeff Billo / Shun-Hsien (Fred) Huang |
| E-mail Address | Jeff.Billo@ercot.com / shuang@ercot.com |
| Company | ERCOT |
| Phone Number | (512) 248-6334, (512) 248-6665 |
| Cell Number |  |
| Market Segment | Not applicable. |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Kelly P. Landry |
| E-Mail Address | klandry@ercot.com |
| Phone Number | 512-248-4630 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| ERCOT 101613 | Proposed revisions to address concerns voiced by affected parties and by stakeholders participating in the 9/18/2013 OWG meeting. |
| ERCOT 012614 | Addressed developer concerns that applying the proposed high VRT standard to IRRs that had not synchronized with the ERCOT System by August 30, 2013 is unnecessary. |
| EDF RE 021214 | Proposed that: (1) a grandfather exemption be granted for those IRRs that have, as of January 16, 2014, both executed an SGIA and provided all required financial security to the TSP; and (2) the compliance date for noncompliant wind resources that do not meet the grandfather exemption be January 16, 2016. |
| EMMT 033114 | Proposed that a grandfather exemption be granted for all projects that are already under development prior to the effective date of NOGRR124. |
| Invenergy 040114 | Proposed that a grandfather exemption be granted for all projects that are in the late stages of development, are commercially online, have executed financial hedge agreements, or have procured substantial equipment. |
| ERCOT 040214 | Addressed the concerns raised by the 03/31/14 EMMT and 04/01/14 Invenergy comments. |

Revised Proposed Guide Language

2.9.1	Additional Voltage Ride-Through Requirements for Intermittent Renewable Resources

(1)	All Intermittent Renewable Resources (IRRs) shall also comply with the requirements of this Section, except as follows:

(a)	An IRR that  interconnects to  the ERCOT System pursuant to a Standard Generation Interconnection Agreement (SGIA) (i) executed on or before January 16, 2014and (ii) under which the IRR provided all required financial security to the TSP on or before January 16, 2014, is not required to meet any high VRT requirement greater than 1.1 per unit voltage unless the interconnected IRR includes one or more turbines that differ from the turbine model(s) described in the SGIA (including any attachment thereto), as that agreement existed on January 16, 2014.  Notwithstanding the foregoing, if the Resource Entity that owns or operates an IRR that was interconnected pursuant to an SGIA executed before January 16, 2014, under which the IRR provided all required financial security to the TSP on or before January 16, 2014, demonstrates to ERCOT’s satisfaction that the high VRT capability of the IRR is not lower than the capability of the turbine model(s) described in the SGIA (including any attachment thereto), as that agreement existed on January 16, 2014 that IRR is not required to meet the high VRT requirement in this Section.

(b)	An IRR that interconnects to the ERCOT System pursuant to an SGIA executed prior to November 1, 2008 is not required to meet VRT requirements presented in this Section.  However, any WGR that is installed on or after November 1, 2008 and that initially synchronizes with the ERCOT System, pursuant to a Standard Generation Interconnection Agreement (SGIA) (i) executed on or before January 16, 2014, and (ii) under which the IRR provided all required financial security to the TSP on or before January 16, 2014(except for an IRR installed pursuant to an SGIA executed before November 1, 2008) shall be VRT-capable in accordance with the low VRT requirements in this Section and high-voltage requirements in this Section up to 1.1 per unit voltage unless the interconnected IRR includes one or more turbines that differ from the turbine model(s) described in the SGIA (including any attachment thereto), as that agreement existed on January 16, 2014 in which case the IRR shall also be required to comply with the high VRT requirements of this section, subject to the exemption described in paragraph (a), above..

(c)	An IRR that is not technically capable of complying with a 1.2 per unit voltage high VRT requirement and that is not subject to either of the exemptions described in paragraphs (a) or (b), above, is not required to meet any high Voltage Ride-Through (VRT) requirement greater than 1.1 per unit voltage until January 16, 2016

(d)	Notwithstanding any of the foregoing provisions, an IRR’s VRT capability shall not be reduced over time.

(2	)	Each IRR shall provide technical documentation of VRT capability to ERCOT upon request.

(3)	Each IRR is required to set generator voltage relays to remain in service for at least 0.15 seconds during all transmission faults and to allow the system to recover as illustrated in Figure 1, Default Voltage Ride-Through Boundaries for IRRs, below.  Recovery time to 90% of per unit voltage should be within 1.75 seconds.  Faults on individual phases with delayed clearing (zone 2) may result in phase voltages outside this boundary but if the phase voltages remain inside this boundary, then generator voltage relays are required to be set to remain connected and recover as illustrated in Figure 1.

(4)	Each IRR shall remain interconnected during three-phase faults on the ERCOT System for a voltage level as low as zero volts with a duration of 0.15 seconds as measured at the Point of Interconnection (POI) unless a shorter clearing time requirement for a three-phase fault specific to the generating plant POI is determined by and documented by the TSP in conjunction with the SGIA.  The clearing time requirement shall not exceed nine cycles.

(5)	Each IRR shall set generator voltage relays to remain interconnected to the ERCOT System during the following high-voltage conditions, as illustrated in Figure 1: any per-unit voltage equal to or greater than 1.175 but less than 1.2 for up to 0.2 seconds, any per-unit voltage equal to or greater than 1.15 but less than 1.175 per unit voltage for up to 0.5 seconds, and any per-unit voltage equal to or greater than 1.1 but less than 1.15 for up to 1.0 seconds.  The indicated voltages are measured at the POI.

(6)	An IRR may be tripped Off-Line after the fault clearing period if this action is part of an approved Special Protection Systems (SPSs).

(7)	VRT requirements may be met by the performance of the generators; by installing additional reactive equipment behind the POI; or by a combination of generator performance and additional equipment behind the POI.  VRT requirements may be met by equipment outside the POI if documented in the SGIA.

(8)	If an IRR fails to comply with the clearing time or recovery VRT requirement, then the IRR and the interconnecting TSP shall be required to investigate and report to ERCOT on the cause of the IRR trip, identifying a reasonable mitigation plan and timeline.

Figure 1:  Default Voltage Ride-Through Boundaries for IRRs.