| NPRR Number | 562 | NPRR Title | Subsynchronous Resonance |
| --- | --- | --- | --- |
| Date |  | April 17, 2014 |  |
| Submitter’s Information |  |  |  |
| Name |  | Randy Jones |  |
| E-mail Address |  | rajones@calpine.com |  |
| Company |  | Calpine |  |
| Phone Number |  | 713.830.8846 |  |
| Cell Number |  | 832.385.3322 |  |
| Market Segment |  | Independent Generator Segment |  |

Comments

Calpine appreciates the opportunity to submit these comments on NPRR562.  We are encouraged by ERCOT staff’s willingness to modify the language based on stakeholder input in the workshops to date.  These proposed Calpine edits and comments are provided on top of ERCOT’s filed comments dated 040914.

Calpine continues to assert that SSO risk to its generating resources is an unintended consequence of transmission system expansion decisions by other parties that we had no part in and we should be held whole in all respects in regard to damages both physical and financial.  SSO has the potential to render a generating asset damaged beyond use without the possibility of operator awareness or intervention.  Replacement power costs with today’s system-wide price caps in place can become catastrophic whether a generating unit is seriously damaged or simply forced offline as part of a protection procedure.  While Calpine may be in agreement with the study provisions and procedural approaches in ERCOT’s latest comments, we feel strongly that the language in this NPRR do not begin to cover any of the risk that certain generation owners may face through no fault of their own.

We understand ERCOT staff’s desire to move this NPRR to Board approval to establish rules for new interconnecting entities timely but implicit in our agreement with the NPRR’s proposed procedures is the understanding that ERCOT and stakeholders must proceed to use this market’s cost-causation principles to determine which parties shall shoulder the cost responsibility for SSO risks.  At the Protocol Revision Subcommittee meeting on April 10th stakeholders discussed at length the Cost Allocation aspect of the NPRR.  Calpine’s position at this point is that the cost of SSO mitigation and protection measures is such a polarized issue that the solution will likely come from the PUCT.  However, since ERCOT did not eliminate section 3.21.3 Cost Allocation in their latest comments we propose significant edits to that section.  We do not believe that incumbent Generation Resources should incur unhedgable costs for risks they could not have anticipated and were not a party to creating.  From an operations standpoint we believe that any procedural approaches to dealing with potential SSO conditions should always first involve bypassing the series capacitance devices.

Lastly, Calpine believes the only sure way to eliminate SSO risks until all protection and mitigation measures called for are implemented is for ERCOT to ensure that the series capacitance devices that are the cause of SSO remain bypassed.  We understand that the series capacitors associated with risk to our identified generating units are bypassed and we expect ERCOT to keep them out of service until all required measures in 3.21.3 have been implemented.

| Revised Cover Page Language |  |  |  |
| --- | --- | --- | --- |
| NPRR Number | 562 | NPRR Title | Subsynchronous Oscillation |

Revised Proposed Protocol Language

2.1 	DEFINITIONS

Subsynchronous Oscillation (SSO)

Coincident oscillation occurring between two or more Transmission Elements or Generation Resources at a natural harmonic frequency lower than the normal operating frequency of the ERCOT System (60 Hz), including, but not limited to, the following types of interactions:

- Subsynchronous resonance – the torsional interaction between series capacitors and turbine-generators.

- Subsynchronous torsional interaction – the interaction between active Transmission Elements (e.g. high-voltage direct current or Static Var Compensator) and turbine-generators.

- Induction generator effects – interactions involving the electrical network only between series capacitors and Generation Resources.

- Subsynchronous control interaction – the amplification of subsynchronous currents due to positive feedback between series capacitors and the control systems of certain Generation Resources.

2.2	ACRONYMS AND ABBREVIATIONS

SSO		Subsynchronous Oscillation

FIS		Full Interconnection Study

3.21	Subsynchronous Oscillation

3.21.1	Initial Identification and Evaluation of Subsynchronous Oscillation Risk

(1)	Subsynchronous Oscillation (SSO) screening studies, including frequency scans, shall be performed by ERCOT in consultation with the interconnecting Transmission Service Provider (TSP) to evaluate a Generation Resource’s risk of becoming radial or near radial to a Transmission Element or Facilities capable of causing SSO.  In the case of a new Generation Resource, ERCOT’s initial evaluation and screening studies shall occur through the ERCOT Generator Interconnection Screening study process provided in the ERCOT Planning Guide. In the case of a change to the topology of the ERCOT Transmission Grid, ERCOT’s initial evaluation and screening studies shall occur through ERCOT’s review of transmission project proposals submitted through the ERCOT Regional Planning process pursuant to Section 3.11, Transmission Planning, and ERCOT’s review of transmission project updates.

(2)	If the screening study shows an SSO risk in the case of six or fewer concurrent Transmission Element Outages in the converged power flow case, then a detailed SSO risk study shall be performed by a designated TSP for a new Generation Resource.

(3)	If ERCOT’s review of transmission project proposals submitted through the ERCOT Regional Planning process shows an SSO risk in the case of six or fewer concurrent Transmission Element Outages in a converged power flow case, then a detailed SSO risk study shall be performed by a designated TSP for the changes to the topology of the ERCOT Transmission Grid.

(4)	If ERCOT deems a detailed SSO risk study necessary, the provision for such study shall be as follows:

(a)	The designated TSP shall be the TSP owning the series capacitor or active Transmission Element involved in the SSO risk, unless another TSP is selected to perform the study by mutual agreement of the TSPs.

(b)	If more than one TSP owns series capacitors or Transmission Elements involved in the SSO risk, the TSPs shall mutually agree on the designated TSP to perform the detailed SSO risk study.

(c)	If the TSPs do not mutually agree on a designated TSP to perform the detailed SSO risk study, then ERCOT shall select one of the TSPs owning Transmission Facilities involved in the SSO risk or the Interconnecting Entity to perform the detailed study.

3.21.2	Detailed Subsynchronous Oscillation Studies

(1)	The designated TSP shall develop a comprehensive scope, including contingencies, for the detailed SSO risk study and distribute it to ERCOT and the other affected Resource Entities and TSPs for comment.  ERCOT shall issue its comments within ten Business Days from receipt of the study scope.

(2)	The detailed SSO risk study report shall include a survey of and recommendation for possible mitigation and protection measures if needed, as defined below in Section 3.21.3. The designated TSP may engage a third-party consultant for this study.

(3)	Generation Resource Data – The specificity of the study and any associated recommendations are directly related to and dependent on the accuracy of the data provided regarding the generation elements that may be at risk of SSO.

    - Upon the request of ERCOT or the designated TSP, any affected Resource Entity shall provide the available data necessary to model the Generation Resource for the purpose of analyzing SSO risk.

    - If the requested data is proprietary and/or confidential, beyond the reasonable control of the affected Resource Entity and can only be obtained from a manufacturer or from another third party, a non-disclosure agreement may be necessary between the manufacturer or third party and the designated TSP, its consultant, if any, and ERCOT.  Detailed models obtained pursuant to a non-disclosure agreement as part of a detailed SSO risk study shall not be used for any other purpose and shall not be disclosed to other parties.

    - If data is not available from the affected Resource Entity and cannot be obtained from a manufacturer or third party, then the designated TSP or its consultant, if any, may make reasonable assumptions in the study.

(4)	Transmission Equipment Data – The specificity of the study and any associated recommendations are directly related to and dependent on the accuracy of the data provided regarding the Transmission Elements that may affect the risk of SSO.

    - Upon request from ERCOT or the designated TSP, any affected TSP shall provide the available data necessary to model the Transmission Element for the purpose of analyzing SSO risk.

    - If the requested data is proprietary and/or confidential, beyond the reasonable control of the affected TSP and can only be obtained from a manufacturer or from another third party, a non-disclosure agreement may be necessary between the manufacturer or third party and the designated TSP, its consultant, if any, and ERCOT.  Detailed models obtained pursuant to a non-disclosure agreement as part of a detailed SSO risk study shall not be used for any other purpose and shall not be disclosed to other parties.

    - If data is not available from the affected TSP and cannot be obtained from a manufacturer or third party, then the designated TSP or its consultant, if any, may make reasonable assumptions in the detailed SSO risk study.

(5)	The detailed SSO risk study shall be reviewed as follows:

(a)	The designated TSP shall present the draft detailed SSO risk study report to ERCOT, affected Resource Entities, and the affected TSPs for comment.  Where multiple Generation Resources are impacted, confidential data shall be redacted in the study report provided to Resource Entities.

(b)	Any questions, comments, proposed revisions, or clarifications by any Entity shall be made in writing to the designated TSP within ten Business Days after receipt of the draft detailed SSO risk study.  ERCOT may extend this review period by an additional 20 Business Days by notifying the designated TSP that it needs additional time to review the draft study report.  ERCOT may request additional data from the affected TSPs and Resource Entities.  ERCOT may further request that the designated TSP conduct additional analysis.

- After considering the information received from ERCOT, affected Resource Entities, and affected TSPs, the study shall be deemed complete and the designated TSP shall issue the final detailed SSO risk study report to ERCOT, affected Resource Entities, and affected TSPs.  Where multiple Generation Resources are impacted, confidential data shall be redacted in the study report provided to Resource Entities.

- ERCOT may deem a detailed SSO risk study not necessary if an Interconnecting Entity and/or Resource Entity synchronizing the new Generation Resource, or TSP provide documentation stating that its equipment is protected against all levels of SSO risk based on the criteria identified in paragraph (2) of Section 3.21.3.  ERCOT shall review any documentation provided with other impacted Resource Entities and TSPs to determine whether further analysis is needed.

3.21.3 	Subsynchronous Oscillation Protection and Mitigation Measures

(1)	Protection and/or Mitigation measures described in this Section may be necessary as a result of a detailed SSO risk study conducted pursuant to Section 3.21.2.  For purposes of this Section, the terms “Protection” and “Mitigation” shall have the following meaning:

(a)	“Protection” shall refer to an automatic switching action that removes the affected Generation Resource and/or Transmission Element from service.

(b)	“Mitigation” shall refer to the installation and use of any equipment or the implementation of any procedure that may be used to mitigate or eliminate SSO risk.

(i)	“Structural Mitigation” shall refer to installation and use of equipment that does not require operator action.  As applied to Transmission Facilities, this may include Special Protection Systems (SPSs), active or passive filters, thyristor-controlled series capacitors, and series capacitor segmentation, construction of new Transmission Facilities, etc.  As applied to the Generation Resource, this may include Special Protection Systems (SPSs), passive filters, mechanical redesign, damping controllers, etc.

(ii)	“Procedural Mitigation” shall refer to implementation of any procedure involving operator action that may be used to mitigate or eliminate SSO risk, such as Outage Coordination, monitoring tools, series capacitor bypass and series capacitor segmentation.  ERCOT and the TSP requesting an Outage, clearance, or switching action shall review such actions for possible SSO risk.

(2)	The use of Protection and Mitigation measures shall be determined by assessing the nature of the SSO risk. The number of concurrent Transmission Element Outages shall be considered an indicator of the risk.

|  | Potential Risk | Action | Responsible Entity |
| --- | --- | --- | --- |
| (a) | n-3 or fewer concurrent Transmission Outages | Protection and Structural Mitigation | All impacted |
| (b) | n-4 or fewer concurrent Transmission Outages | Protection | All impacted |
| (c) | n-4, n-5, n-6 concurrent Transmission Outages | Procedural Mitigation | All impacted and ERCOT |

(3)	All impacted Entities shall agree to the coordination and selection of the implemented solution(s).

(4)	The Protection and Mitigation measures required in this Section are minimum requirements and do not preclude an affected Entity from implementing additional measures.

(5)	Approval and Reporting of Protection and/or Mitigation Measures.

(a)	ERCOT shall review the final detailed SSO risk study and approve, reject or recommend modification of Protection and/or Mitigation measures with 30 days of receipt of the study.

(b)	ERCOT shall incorporate conclusions regarding SSO risk, including level of study and approved Protection and/or Mitigation measures, in its future studies or reviews for transmission planning projects.

(6)	Cost Allocation.

(a)	SSO Studies.  The Entity introducing the new Transmission Element, new Generation Resource, or switching practice identified as creating a potential SSO risk shall be responsible for the cost of all SSO studies and all costs of protection and mitigation on all affected Generation Resources identified in the SSO study.

(b)	Protection.  The cost of any protective equipment shall be the responsibility of the Entity whose Transmission Element or new Generation Resource is identified as creating a potential SSO risk.

(c)	Structural Mitigation.  The cost of any equipment necessary to implement Structural Mitigation shall be the responsibility of the Entity whose Transmission Element or new Generation Resource is identified as creating a potential SSO risk.

(7)	Modification of Mitigation Measures.  Any proposed change to an ERCOT-approved Mitigation measure associated with SSO risk shall be submitted to all affected Entities and approved by ERCOT and the affected Facility Owners in writing before taking effect.  ERCOT shall approve or reject the proposed change within 90 days of notification.