ERCOT Synchronous Inertial Response Service

Working Document – Work Session (5-2-2014):

# Need for SIR Service

Synchronous Inertial Response (SIR) is an immediate response that is continuously self-deployed from synchronous machines  to compensate for power imbalance and is a key determinant of the strength and stability of the power system.

Synchronous Inertial Response has significant implications on the rate of change of frequency (RoCoF) following a disturbance.  With increasing non-synchronous generation SIR is reduced and RoCoF increases, leaving insufficient time for PFR to deploy and arrest system frequency, i.e. time between point A and C, Figure 1.  High RoCoF can cause frequency to reach the nadir quickly and trigger under-frequency load shedding of firm loads.  There is a need to assure the provision of a sufficient amount of inertial response on the ERCOT system.  SIR service is intended to meet this need.

Figure 1  Typical frequency response following a generator trip.

# Definition of Synchronous Inertial Response Service

Protocol Definition for Synchronous Inertial Response Service –Concept Level acceptance requested prior to Protocol Language development– Consensus (XXXX%) Synchronous Inertial Response (SIR) is defined as the kinetic energy (at nominal frequency) that is extracted from the rotating mass of a synchronous machine to compensate an imbalance in a power system. The kinetic energy (in MW-seconds) is based on the commissioned design capability of the Resource. It can be determined through appropriate validation procedures based on the following relationship: - J is the combined moment of inertia of a synchronous machine and turbine prime mover in kg·m2, based on its size and weight; - o is the nominal machine rotor speed in rad/s, and - PMVA is the machines rated capacity in Mega Volt – Amperes. - H is the figure of merit used to analyze the synchronous machine’s inertial response and is referred to as the machine’s inertia constant in seconds. From the above expression H is: The inertial response that a synchronous machine can provide is independent of the machine’s power output and can be evaluated based on machine parameters (H and rated MVA) and machine status (online/offline).

ERCOT needs to verify that consistent MVA rating is used for both H constant and SIR calculation.

- Deployment, Sustain and Recall Requirements for Synchronous Inertial Response

Protocol Definition for Synchronous Inertial Response Service –Concept Level acceptance requested prior to Protocol Language development– Consensus (XXXX%) Synchronous Inertial Response is immediately self-deployed from online synchronous machines to compensate for an imbalance in a power system. SIR is self-recovering as reserves (FFR, PFR, and Regulation) are deploying after initial frequency deviation. When the system frequency returns to nominal, the SIR is fully recovered.

- Performance Measurement

Protocol Definition for Synchronous Inertial Response Service –Concept Level acceptance requested prior to Protocol Language development– Consensus (XXXX%) Performance of a Resources providing SIR is ensured as long as a Resource is synchronized with the ERCOT grid. Whenever a Resource is online its Synchronous Inertial Response will be calculated as: SIR = H·MVA,

- Limits on Resources providing Synchronous Inertial Response

Protocol Definition for Synchronous Inertial Response Service –Concept Level acceptance requested prior to Protocol Language development– Consensus (XXXX%) Resource providing SIR is limited based on Resource’s inertial constant H, nameplate MVA rating. SIR=H⋅MVA

Figure 2 Inertial response of ERCOT generation fleet by unit type.

*HY: Hydro, CA:  Combustion turbine as part of a Combined Cycle Plant, GT: Gas Turbine, ST: Steam Turbine, CT: Combustion Turbine, NU: Nuclear

# Qualification of Resources Providing Synchronous Inertial Response

Protocol Definition for Synchronous Inertial Response Service –Concept Level acceptance requested prior to Protocol Language development– Consensus (XXXX%) Resources that operate synchronously with ERCOT grid can qualify for SIR service based on the commissioned design capability of the Resource as determined through appropriate testing procedures. Resource should provide ERCOT with the following parameters: - Inertial constant H and - Corresponding MVA base

# Methodology to Determine Requirement for Synchronous Inertial Service

Total inertial contribution  from all synchronous machines, committed for energy and AS, must achieve the required system inertial response. PFR and FFR requirements are always based on certain system inertia level. Minimal inertial response requirement should be such that after two largest units trip (currently 2750 MW) SIR, PFR and FFR should ensure fnadir ≥ 59.4 Hz, that is 0.1 Hz above the prevailing initial threshold of Firm Load UFLS (59.3 Hz).

ERCOT will develop specific criteria for determination of minimum SIR requirement. To provide an example, if the target for the inertia requirement is to have the system frequency no less than 59.4 Hz after 0.5 seconds (RoCoF = 1.2 Hz/second) following two largest unit trip (2750 MW), the calculated minimum SIR requirement is estimated about 78 GW-second (at 24857 MW load and 2.44% per Hz load damping). The required amounts of PFR and FFR are expected to be significantly increased under low inertia condition. There may be other considerations, such as RoCoF tolerance, which can set additional limit on SIR requirement.

If synchronous condensers are owned and operated by TDSPs, the TDSPs are not expected to be eligible for SIR payments. Inertial response contribution provided by online synchronous condensers owned by TDSPs will be taken into account when determining minimum SIR requirement.

Based on current operations data the RoCoF during high wind low load condition was less than 0.2 Hz/second and the average time to reach frequency nadir during frequency events is within 4 to 6 seconds. Therefore, the system inertia available in the real time operations under current conditions is sufficient.

Studies based on 2013-2014 system conditions (presented at FAST Workshop on 3/28/2014) indicated RoCoF as high as 0.45 Hz/s for two largest unit trip (2750 MW as per recently approved NERC BAL-003 standard).

Table 1 shows presented at FAST Workshop on 3/28/2014 and two recent penetration record cases showing system inertia.

Table 1. System Inertia (GW-seconds) under different system conditions

| Case | Date/Time | Load (MW) | Wind Output (MW) | PRC (MW) | Wind Penetration | Net Load (MW) | System Inertia GW-seconds |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 08072013 17:00 | 67,148 | 2,398 | 4,105 | 3.57% | 64,750 | 372 |
| 2 | 02132014 19:00 | 36,460 | 1,188 | 5,062 | 3.26% | 35,272 | 236 |
| 3 | 01132014 03:00 | 24,857 | 7,196 | 5,812 | 28.95% | 17,661 | 174 |
| 4 | 03272014 3:19 | 25,677 | 9,868 | 5,826 | 38.43% | 15,809 | 148 |
| 5 | 03312014 02:12 | 24618 | 9,699 | 5,152 | 39.4% | 14,919 | 135 |

These data show a potential trend of SIR decreasing with increasing amounts of non-synchronous generation.

The determination of requirements for SIR, FFR and PFR are interrelated. How much of one type is required depends on how much of the other is available. ERCOT will develop methodology for SIR, PFR and FFR requirements.

# Discussion on SIR service implementation

Sufficient SIR needs to be maintained for every hour of a year. It is expected most of the time sufficient amount of synchronous inertia will be provided by synchronous machines committed for energy. The need for additional inertia might only arise during low load, high wind situations, about 15% of time (in 2013) according to Figure 3. Every online machine qualified to provide synchronous inertial response should be compensated for SIR service.

Figure 3  Distribution of netload levels in 2013

Synchronous machines will provide all of its SIR whenever synchronized with the grid. The amount of SIR provided does not depend of unit output and does not require capacity reservation that can be co-optimized with energy similarly to other AS. SIR procurement is expected to be a commitment process.

However in the Day Ahead Market the Resource participation is voluntary, therefore it is not transparent in DAM what Resources will be committed for energy and/or AS and be providing SIR inherently. Introduction of the procurement process (commitment process) for SIR in DAM will require changes to the DAM. Otherwise, the SIR procurement (commitment process) needs to be initiated after DAM closure and when COPs become available.

Note that insufficient inertia conditions usually occur at high wind low load situations. It is desirable that synchronous machines brought online to ensure sufficient inertia response have low minimum power output. This prevents oversupply situations and negative impact on energy prices.

ERCOT RATF (Resource Adequacy Task Force) is currently discussing issues of Reliability Unit Commitment and mitigating its impact on RT market prices. The outcome of these discussions can also apply for mitigating the pricing impacts due to commitment for SIR procurement.

Existing Generation Resources capable of providing SIR can explore their capability to de-clutch between turbine and synchronous generator so as to operate in synchronous condenser mode and provide SIR without injecting energy to the grid

- Synthetic/Emulated Inertia

SIR product comes from the immediate response of the Resource to an event and while de-synchronized Resources (e.g. battery storage, Type III and IV WGRs, future commercial DC-ties) may be able to react very quickly there will be a moment in time where an inertial response is required but not provided.  For this reason at this stage ERCOT does not consider it appropriate to extend the definition of the SIR Service to providers who are not synchronized. However, ERCOT recognizes that there is a potential value to such emulated inertial response, and will create Emulated Inertial Response service as a separate ancillary service. ERCOT will continue follow up the synthetic inertial response technology to identify the potential benefits to the ERCOT system.

# Conclusions from the FAST Working Session 04-25-2014

The system inertia available in the real time operations under current operating conditions is sufficient. Table 1 shows a potential trend of SIR decreasing with increasing amounts of non-synchronous generation. Based on the feedback from the FAST Work Session on April 25, 2014, ERCOT will undertake the following steps prior to introducing SIR as a Service:

- ERCOT will start monitoring real time inertia, MVA*H and provide summaries to the stakeholders.

- ERCOT will analyze unit commitment patterns to identify likely periods with low inertia.  Then, ERCOT will study the projected synchronous inertia trends for low load high wind situations with 2-3 years look-ahead.

- Once projections show insufficient inertia for the future, ERCOT will initiate the stakeholder process to discuss SIR needs. In the meantime, Reliability Unit Commitment for inertia may be used in interim.

- ERCOT will develop methodology to determine minimum SIR needs. Inertial response contribution provided by online synchronous condensers owned by TDSPs will be taken into account when determining minimum SIR requirement.

- ERCOT will continue to investigate the potential system impact of high RoCoF.

- ERCOT will continue monitoring low SIR mitigation measures implemented in other regions with high penetration of non-synchronous generation (like Tasmania, Ireland, Hydro Quebec).

ERCOT Emulated Inertial Response (EIR) Service

Discussion Document – Work Session (4-25-2014):

Through proper controller settings, EIR Resources can monitor the system frequency and continuously provide fast acting response with respect to frequency deviations.

A proposed 10 seconds support was tested and presented at the Worksesson on 4/18/2014 http://www.ercot.com/content/meetings/fast/keydocs/2014/0418/10sec_support_test_04172014.pdf. The Resources deploy 50% of the obligation (within 5 cycles) when frequency is at 59.9 Hz and be fully deployed (within 5 cycles) when frequency reaches 59.8 Hz.  The Resources automatically recall the deployment after a 10 seconds deployment.  Assuming such 10 seconds providing the EIR, figure below shows the response compared to the proposed FFR service.  It can be shown that the undesirable effect of quick withdrawal of such 10 seconds service.  .

Figure below, as another example, illustrates test results of the wind turbine providing EIR. The wind turbine’s EIR response is dependent on the operating condition that the desirable response without adverse effect on frequency recovery can only be achieved at and above certain output level.

Figure 1 Averaged inertial control response of a tested GE wind turbine. A total of 141 trials were performed, with results grouped into wind speed buckets near 5, 8, 10, 11.5, and 14 m/s. This performance is for a specific set of tuned control parameters [1].

Ref [1] does not provide corresponding plots showing the impact of EIR at different wind speeds on system frequency during generation trip events. Rather it conducts several studies looking at aggregated impact of the entire Irish wind generation fleet based on actual operating conditions of WTGs.

Figure 2 Frequency response for Irish transmission system (in this study case demand is 5588 MW, the non-synch penetration is 70%, 1000-MW HVDC export, and the wind contribution is 4634 MW, and cases are considered when 100%, and only 50%, of wind turbines are fitted with EIR [1].

The study concludes that by reducing number of WTGs providing EIR or tuning the response to being “less aggressive” the frequency level during the recovery can be increased.

The paper concludes that:

- Wind turbine inertia, active power contribution level, and pre-event loading level have a large impact on the recovery phase

- EIR of a single wind turbine is not representative of the response obtained from the whole wind power plant

- The cumulative effect of the recovery phase on system frequency may limit the benefits of SIR as wind penetration increases

- EIR contribution from WGRs need to be tuned as an aggregate across entire fleet of WGRs with EIR capability in order to suit the dynamic response requirements of the particular system and to ensure that system frequency performance is not diminished by EIR addition.

- To determine the aggregate emulated inertial response capability of wind power, a system operator would need to forecast how many wind turbines with EIR are operating above their minimum operating speed and so are capable of contributing with EIR, as well as the operating condition of those turbines and the potential depth and duration of the energy recovery period following the disturbance.

Discussion

- Should/can EIR Resources support both high and low frequency on a continuously basis without a deadband?

In theory EIR of WGRs could work for high frequency events, but in practice manufacturers so far has not implemented such capability. In Ireland, there is concern that a high frequency event could result if a HVDC interconnector in export mode were to trip, but rather than wind turbines providing 'inertial support' they are required to reduce their output once the frequency hits a threshold level.

Comments from the 04/25/2014 Work Session: EIR needs to be proportional, have deadband around 100-500 mHz, self-recall proportional to frequency (deadband should be that the sustain time is limited to about 30 seconds).

EIR from WGRs in not the target technology for this service (future commercial HVDC ties, storage and possibly controllable load resources may be capable to provide EIR).

- What should deployment duration for EIR to avoid adverse impact on frequency recovery? For example WGR providing EIR normally operates slightly below its HSL their Response can be sustained and impact to frequency recovery will not be an issue.

Figure 3 Response of wind generation resources to frequency deviation and corresponding frequency plots from a study conducted by EPRI

- The magnitude of EIR is directly proportional to the output of wind-farm, procuring this service in Day-ahead will not provide certainty that procured EIR will be available in real-time. Currently we are on average slightly below 10% error on day-ahead wind forecast. Literature suggests EIR forecast error is likely to be lower than that of wind power production forecast for the same time horizon however it still introduces additional degree of uncertainty to the response that is essential for the system reliability.

- Some ISOs require WGRs to provide emulated inertial response as a part of the interconnection requirement recognizing that inertial response is essential for system reliability and conventional generators inherently provide it. For example Hydro Quebec requires WGRs > 10 MW to respond to frequency deviations as much as does the inertial response of a conventional synchronous machines with H=3.5 s. The target performance is met, for instance when the system varies its real power dynamically and rapidly by at least 5% for about 10 seconds. Currently HQ is working on the requirements to limit impact form EIR on frequency recovery.

- Performance and measurement for EIR?

- Do FFR1 and FFR2 already provide necessary response similar to EIR with regard to C-point while also improving B-point frequency?

Imbalance between mechanical power and electrical power

Physical Responsive Capability

Wind penetration = Wind Output / Load

Net Load = Load – Wind Output

Lisa Ruttledge, Nicholas W. Miller, Jonathan O’Sullivan, Damian Flynn, “Frequency Response of Power Systems With Variable  Speed Wind Turbines “, IEEE Transactions on Sustainable Energy, Vol. 3, No. 4, October 2012

Lisa Ruttledge, Nicholas W. Miller, Jonathan O’Sullivan, Damian Flynn, “Quantifying the Aggregate Frequency Response from Wind Generation with Synthetic Inertial Response Capability” International Workshop on Large-Scale Integration of Wind Power into Power Systems, London 2013

Hydro Quebec, “Transmission Provider Technical Requirements for Connection of Power Plants to the Hydro-Quebec Transmission System”, February 2009