| NOGRR Number | 132 | NOGRR Title | Automatic Under-Voltage and Under-Frequency Load Shedding Protection Systems – Load Restoration |
| --- | --- | --- | --- |
| Date Posted |  | May 13, 2014 |  |

| Requested Resolution | Normal. |
| --- | --- |
| Nodal Operating Guide Section Requiring Revision | 2.6.1, Automatic Firm Load Shedding 6.2.6.3.6, Automatic Under-Voltage Load Shedding Protection Systems |
| Other Binding Documents Requiring Revision or Related Revision Requests | None. |
| Revision Description | This Nodal Operating Guide Revision Request (NOGRR) adds a requirement for Under-Frequency Load Shedding (UFLS) and Under-Voltage Load Shedding (UVLS) systems Load restoration coordination consistent with that of manually shed Load for EEA 3 or a Constraint Management Plan. |
| Reason for Revision | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) Paragraph (4) of Section 11.4, Mitigation Plan, states, “Restoration of any Load shed by executing the Mitigation Plan shall be coordinated with ERCOT.” To improve reliability of the ERCOT System, ERCOT proposes similar language in Section 6.2.6.3.6 to provide a reasonable level of assurance that Load restoration will not exceed capability limits of Generation Resources or Transmission Facilities. Additionally, ERCOT proposes to use similar language in Paragraph (5) of Section 2.6.1 for consistency and clarity that coordination is expected for any of the Load shed restoration with UFLS, UVLS, or Constraint Management Plans with Load shed. |

| Business Case |  |  |
| --- | --- | --- |
| Qualitative Benefits | - Improved reliability by documenting and requiring Load shed as a result of UVLS to be restored to a level that would not overload limits - Aligns with current ERCOT business practices - Clarifies rules as current rules provide specific language surrounding load restoration for UFLS, Constraint Management Plans, and EEA3 load shed instructions, but does not specifically address UVLS load shed restoration. Language clarifies there is an expectation to coordinate with ERCOT ISO. |  |
| Quantitative Benefits |  |  |
| Impact to Market Segments |  |  |
| Credit Implications |  |  |
| Other |  |  |
| Sponsor |  |  |
| Name |  | Stephen Solis |
| E-mail Address |  | ssolis@ercot.com |
| Company |  | ERCOT |
| Phone Number |  | (512) 248-6772 |
| Cell Number |  |  |
| Market Segment |  | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Brian Manning |
| E-Mail Address | Brian.manning@ercot.com |
| Phone Number | 512-248-3937 |

Proposed Guide Language Revision

2.6	Requirements for Under-Frequency Relaying

2.6.1	Automatic Firm Load Shedding

(1)	At least 25% of the ERCOT System Load that is not equipped with high-set under-frequency relays shall be equipped at all times with provisions for automatic under-frequency load shedding.  The under-frequency relays shall be set to provide Load relief as follows:

| Frequency Threshold | Load Relief |
| --- | --- |
| 59.3 Hz | 5% of the ERCOT System Load (Total 5%) |
| 58.9 Hz | An additional 10% of the ERCOT System Load (Total 15%) |
| 58.5 Hz | An additional 10% of the ERCOT System Load (Total 25%) |

(2)	With the assistance of applicable Transmission Service Providers (TSPs), ERCOT will, prior to the peak each year, survey each Distribution Service Provider’s (DSP’s) compliance with the automatic Load shedding steps above, and report its findings to the Technical Advisory Committee (TAC).  For minimum compliance, DSPs are obligated to meet the prescribed percent values at all times.  It is not permitted to use rounding to meet the minimum.  ERCOT will direct a review of the automatic firm Load shedding program whenever warranted by conditions.  At a minimum, this review will follow the Reliability and Operations Subcommittee (ROS) directed dynamic simulations of automatic firm Load shedding conducted at five-year intervals beginning in the Summer of 2001.

(3)	Additional under-frequency relays may be installed on Transmission Facilities with the approval of ERCOT provided the relays are set at 58.0 cycles or below, are not directional, and have at least 2.0 seconds time delay.  A DSP may by mutual agreement arrange to have all or part of its automatic Load shedding requirement performed by another entity.  ERCOT will be notified and provided with the details of any such arrangement prior to implementation.

(4)	DSPs shall ensure, to the extent possible, and under the direction of ERCOT, that Loads equipped with under-frequency relays are dispersed geographically throughout the ERCOT Region to minimize the impact of Load shedding within a given geographical area.  Customers equipped with under-frequency relays shall be dispersed without regard to which Load Serving Entity (LSE) serves the customer.  DSPs shall ensure that the under-frequency relays connected to each Load will operate with a fixed time delay of no more than 30 cycles.  Total time from the time when frequency first reaches one of the values specified above to the time Load is interrupted should be no more than 40 cycles, including all relay and breaker operating times.  If the frequency drops below 58.5 Hz, ERCOT shall determine additional steps to continue operation.

(5)	If a loss of Load occurs due to the operation of under-frequency relays, a Transmission Operator (TO) designated by a DSP to shed Load may rotate the physical Load interrupted to minimize the duration of interruption experienced by individual Customers or to restore the availability of under-frequency Load-shedding capability.  In no event shall the initial total amount of Load without service be decreased by a TO without the approval of ERCOT.  TOs, in coordination with DSPs, shall make every reasonable attempt to restore Load, either by automatic or manual means, to preserve system integrity.  TOs, in coordination with DSPs, shall exercise extreme caution in restoring Load so that the capability limits of Generation Resources and Transmission Facilities are not exceeded.  Restoration of any Load shed by Under-Frequency Load Shedding  (UFLS) systems shall be coordinated with ERCOT.

(6)	Whenever possible, TOs and DSPs shall not manually drop Load connected to under-frequency relays during the implementation of Level 3 of an Energy Emergency Alert (EEA).

6.2.6.3.6	Automatic Under-Voltage Load Shedding Protection Systems

(1)	Automatic Under-Voltage Load Shedding (UVLS) systems are classified as protective relay systems. The maintenance requirements, discussed in Section 6.2.5, Maintenance and Testing Requirements for ERCOT System Facilities, apply to UVLS protection systems as well.

(2)	The requirement for under-voltage relaying shall be determined by system studies performed/administered by ERCOT designated working groups or equipment owners. The system studies should indicate the following:

(a)	Amount of Load to be shed to restore voltage to minimum acceptable level or higher;

(b)	The minimum and maximum time delay allowed before automatically shedding Load;

(c)	The voltage level(s) at which to initiate automatic relay operation; and

(d)	The location(s) for effectively applying UVLS protection systems.

(3)	Automatic UVLS protection systems need not be duplicated.

(4)	Analyses shall be performed on UVLS schemes by working groups and/or equipment owners as assigned by ERCOT to demonstrate that they are expected to act before generators trip Off-Line due to the protective relay requirements, as specified in paragraph (3)(a) of Section 2.9, Voltage Ride-Through Requirements for Generation Resources.  A specific exemption from this analysis requirement may be provided by the ROS.

(5)	Under-voltage protection systems shall be designed to coordinate with other protective devices and control schemes during momentary voltage dips, sustained faults, low voltages caused by stalled motors, motor starting, etc.

(6)	Automatic Load restoration for an UVLS operation is not currently utilized in ERCOT.

(7)	The UVLS scheme shall be designed to ensure reliable operation and to prevent false tripping.

(8)	In addition, protective relaying for Generation Resources must be designed to meet Voltage Ride-Through (VRT) criteria as detailed in Section 2.9.

(9) 	Restoration of any Load shed by UVLS shall be coordinated with ERCOT.