| NOGRR Number | 129 | NOGRR Title | Implement Operational Preparedness for Geomagnetic Disturbances |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Recommended Approval |
| Date of Decision |  | May 19, 2014 |  |  |
| Proposed Effective Date |  | July 1, 2014 |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Nodal Operating Guide Sections Requiring Revision |  | 1.4, Definitions 4.7, Geomagnetic Disturbance Operating Plan (new) 4.7.1, Monitoring and Dissemination of Space Weather Information (new) 4.7.2, Development and Submission of TO GMD Operating Procedures or Processes (new) 4.7.3, ERCOT’s GMD Operating Plan and Review of TO GMD Operating Procedures or Processes (new) |  |  |
| Other Binding Documents Requiring Revision or Related Revision Requests |  | None. |  |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) sets up an ERCOT Region coordination process through which ERCOT and Transmission Operators (TOs) will develop Geomagnetic Disturbance (GMD) operating documents and communicates such information. |  |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) |  |  |
| Procedural History |  | - On 3/12/14, NOGRR129 was posted. - On 4/16/14, Austin Energy comments were posted. - On 4/22/14, ERCOT comments were posted. - On 4/23/14, the Operations Working Group (OWG) considered NOGRR129. - On 5/7/14, an Impact Analysis was posted. - On 5/19/14, OWG considered the 4/23/14 OWG Report and Impact Analysis for NOGRR129. |  |  |
| OWG Decision |  | On 4/23/14, OWG was in consensus to recommend approval of NOGRR129 as amended by the 4/22/14 ERCOT comments. On 5/19/14, OWG was in consensus to endorse and forward the 4/23/14 OWG Report and Impact Analysis for NOGRR129 to ROS. |  |  |
| Summary of OWG Discussion |  | On 4/23/14, participants discussed the merits of NOGRR129, how to address GMD in the Nodal Operating Guides versus in the North American Electric Reliability Corporation (NERC) Standards, and the potential for one or more related workshops. On 5/19/14, participants discussed coordination of reports and the general impact of GMD on the ERCOT Region. |  |  |

| Business Case |  |
| --- | --- |
| Qualitative Benefits | Allows ERCOT and TOs to meet requirements of NERC Standard EOP-010, Geomagnetic Disturbance Operations, which is pending Federal Energy Regulatory Commission (FERC) approval. |
| Quantitative Benefits |  |
| Impact to Market Segments |  |
| Credit Implications |  |
| Other |  |

| Sponsor |  |
| --- | --- |
| Name | Paul Rocha on behalf of Geomagnetic Disturbance Task Force (GMDTF) |
| E-mail Address | Paul.rocha@centerpointenergy.com |
| Company | CenterPoint Energy |
| Phone Number | 713-207-2768 |
| Cell Number |  |
| Market Segment | Investor Owned Utility (IOU) |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Lisa Trow |
| E-Mail Address | ltrow@ercot.com |
| Phone Number | 512-248-6521 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| Austin Energy 041614 | Proposed changes that would more closely align NOGRR129 with the requirements of the NERC Reliability Standard EOP-010-1. |
| ERCOT 042214 | Provided clarification to the 4/16/14 Austin Energy comments. |

Proposed Guide Language Revision

1.4	Definitions

Geomagnetic Disturbance (GMD)

A disturbance of the earth’s magnetic field caused by the interaction of that field with the effects of solar storms.  These GMDs may result in induced currents that may negatively affect power system equipment.

4.7       Geomagnetic Disturbance Operating Plan

4.7.1	Monitoring and Dissemination of Space Weather Information

(1)	ERCOT shall maintain procedures to receive Geomagnetic Disturbance (GMD) alerts and warnings issued by the National Oceanic and Atmospheric Administration (NOAA).

(2)	ERCOT shall implement and maintain procedures to provide GMD alerts and warnings to Transmission Operators (TOs).

(3)	Other forecasted and current space weather information is publicly available directly through the NOAA website.

4.7.2	Development and Submission of TO GMD Operating Procedures or Processes

(1)	Each TO that operates transmission equipment that includes a power transformer with a high side wye-grounded winding with terminal voltage greater than 200kV shall develop a GMD operating  procedure or process to mitigate the effects of GMD events on the reliable operation of its system.

(2)	Each TO GMD operating procedure or process shall be provided to ERCOT within three months following approval by the Federal Energy Regulatory Commission (FERC) of North American Electric Reliability Corporation (NERC) Standard EOP-010-1, Geomagnetic Disturbance Operations.  Updates to the plan shall be provided to ERCOT by March 15 of each subsequent year.

(3)	Each TO GMD operating procedure or process shall include:

(a)	A procedure to receive GMD alerts and warnings from ERCOT;

(b)	A description of operational actions the TO intends to take to mitigate the effects of a GMD event.  This description shall include:

(i)	The triggering event for each action;

(ii)	A detailed explanation of each operational action;

(iii)	A list of Entities with which the TO must coordinate, if any, including any actions requested of other Entities in the ERCOT Region mn order to implement the TOSs GMD oOerating procedure or process; Pnd

(iv)	The conditions under which each action would be terminated.

(c)	A procedure for reporting to ERCOT any unusual operational information that could be the result of GMD, such as high reactive loading, Mega Volt-Amperes reactive (MVAr) or voltage swings, high geomagnetically induced current on monitored transformers or equipment malfunctions.

    - ERCOT’s GMD Operating Plan and ERCOT Review of TO GMD Operating Procedures or Processes

(1)	ERCOT shall develop a GMD operating plan and post it on the Market Information System (MIS) Public Area.

(2)	The ERCOT GMD operating plan shall coordinate the TO GMD operating procedures or processes. This coordination is intended to ensure the TO GMD operating procedures or processes are not in conflict with one another and is not intended to be a review of the technical aspects of the TOSGMD oOerating procedures or processes.P

(3)	In preparing the ERCOT GMD operating plan, ERCOT shall identify and notify the relevant TOs of any conflicts between the different TO GMD operating procedures or processes and any unacceptable actions requested of ERCOT in the TO operating procedures or processes.

(a)	ERCOT and the TOs shall coordinate development of any required modifications to the TO GMD operating procedures or processes necessary to resolve these conflicts or unacceptable actions.

(b)	A TO shall make the resulting modifications to its GMD operating procedures or processes.

(4) The ERCOT GMD operating plan shall include:

(a) 	A description of activities designed to mitigate the effects of GMD events on the reliable operation of the interconnected transmission system; and

(b) 	Any operating actions required of ERCOT by the TO GMD operating procedures or processes and approved by ERCOT for inclusion in the ERCOT GMD operating plan.