## Slide 1
ERCOT Independent Review: Leander – Parmer Lane – Round Rock 138 kV Project
Technical Advisory Committee (TAC)
May 29, 2014
Prabhu Gnanam, ERCOT Transmission Planning

## Slide 2: Project Background
  Load in western Williamson County (including the cities of Leander and Cedar Park areas) served in part by the Pedernales Electric Cooperative (PEC) -owned Avery Ranch, Balcones, Blockhouse, Buttercup, Kent Street, Leander, Seward Junction, and Whitestone substations have experienced significant growth
    From 2002 to 2012 the summer peak load served by these substations has grown from 183.8 MW to 360.1 MW
    PEC has forecasted these substations to serve 575 MW in 2022
  PEC has identified the need for two new substation to serve the load growth
    One substation near the intersection of Parmer Lane and Highway 1431 (needed by 2019)
    Second substation near the intersection of East Crystal Falls Parkway and Ronald Reagan Boulevard (needed by 2020)
  In addition to the PEC need for new substation, LCRA has identified reliability criteria violations in the area

## Slide 3: Area Map of PEC and LCRA TSC System in Western Williamson County
General Location for New Substation 2
General Location for New Substation 1

## Slide 4: Project Evaluation
  New Parmer Substation is needed to meet PEC load growth by 2019
  No reliability issues were identified in 2019
  Both thermal overloads and low voltages were observed in 2022 (With G-1 condition: Loss of Ferguson Unit)
  Thirteen options were evaluated, all the options connect via the new Parmer Substation.
Branch | Contingency | Loading in 2022
Lago Vista – Nameless 138 kV | Whitestone – Buttercup 138 kV | 106.7%
Hutto – Round Rock NE 138 kV ckt 2 | Techridge – Howard Lane 138 kV | 103.4%

## Slide 5: ERCOT Recommendation
  ERCOT will seek Board of Director endorsement of the following project (Option # 11) as the best option to address both the load growth and reliability needs in the western Williamson County:
  Construct a new Parmer 138 kV Substation
  Construct a new 138-kV single circuit line on a double-circuit capable transmission structure (approximately 12.6 miles) that connects the existing Leander and Round Rock substations to the new Parmer Substation with an emergency rating of at least 446 MVA
  Add terminal equipment at the existing Leander and Round Rock substations for the new transmission line
  Upgrade the 138-kV bus at the Leander Substation
  The cost estimate is $50.96 million

## Slide 7
  APPENDIX

## Slide 8: Project Options
  Thirteen options were evaluated, all the options connect via the new Parmer Substation.
Option | From | To | Estimated Cost ($million)
1 | Chief Brady | Whitestone | 62.30
2 | Chief Brady | Avery Ranch | 60.90
3 | Chief Brady | Jollyville | 63.60
4 | Avery Ranch | Seward Junction | 54.00
5 | Jollyville | Seward Junction | 56.80
6 | Round Rock | Seward Junction | 61.90
7 | Avery Ranch | Leander | 43.10
8 | Jollyville | Leander | 46.20
9 | Chandler | Leander | 54.40
10 | Round Rock S | Leander | 77.50
11 | Round Rock | Leander | 51.00
12 | Chief Brady | Leander | 63.70
13 | Westinghouse South | Leander | 52.40

## Slide 9: 2019 Study Results

## Slide 10: 2022 Study Results