LCRA Comments to FAST Consolidated Working Document (5-6-14)

LCRA offers the following comments to incorporate current protocol language for hydro generation resources providing responsive reserve services to ERCOT.

PFR Service

III. Governor Setting Requirement for Generation Resources

After first sentence of the second paragraph, add “For hydro Generation Resources operating in synchronous condenser fast-response mode, the response may be initiated by automatic under-frequency relay at a set point no less than 59.80 Hz.” This language should be included to accommodate the capability of technology with similar response mechanisms.  It is extremely beneficial for grid stability during frequency excursions to allow this type of technology to operate in this condition.  .

V. Qualification and Limit on Resources Providing PFR

B. Limit on Resources Providing PFR

In the first paragraph, add “Hydro Generation Resources operating in synchronous condenser fast-response mode or with a 5% droop setting may provide PFR up to the proven response capability (which may be 100% of HSL).” Performance testing will show the proven 20-second response capabilities and limiting the MWs is not applicable.  This language should also be incorporated into the grey box Protocol Concept section.

Supplemental Reserve Service

We do not believe that on-line generation resources should be excluded from participating in this ancillary service, although this should be discussed further.