“Consolidated Working Document (5-6-14)”

ERCOT Primary Frequency Response

Working Document – 5-6-14

# Definition of PFR Service

PFR Service is an Ancillary Service that acts without operator action to provide an arresting and/or counter response to frequency deviations and, in this manner, acts to maintain the steady state frequency in the ERCOT Interconnection within defined limits.  A PFR response to frequency disturbances in the ERCOT Interconnection can be provided by online synchronous Generation Resources through the operation of their speed governor or by other types of Resources capable of providing a similar automatic control action in response to frequency deviations.  Resources that provide PFR Service must be able to assist in arresting and stabilizing over or under frequency excursions.  Error: Reference source not found illustrates a PFR Service provider’s frequency response to the loss of generation event.  A PFR Service provider’s Governor is expected to initiate frequency response action shortly following the departure of system frequency outside the Governor Dead-band which then assist in establishing the Frequency Nadir (point “C”) and in restoring system frequency to a stable condition referred to as the Settled Frequency (point “B”).  PFR operates within the first few seconds following the initiating event and is fully delivered within 12 to 14 seconds and thus has significant implications on the rate of change of frequency (RoCoF) during sudden power imbalance.

# Needs of PFR Service

ERCOT is a single Balancing Authority Interconnection and is not synchronously connected with any other interconnections, therefore, ERCOT is solely responsible for maintaining interconnection frequency to ensure reliability and meet NERC standard requirements.  With an increasing amount of non‐synchronous generation (e.g. wind generators) there is a significant possibility this response will be reduced as the result of the economic displacement of generation resources capable of providing the PFR service with the consequence that RoCoF becomes higher, leaving insufficient time for other reserves to deploy and arrest the decline in system frequency before it drops to an unacceptable level.  The ability of the ERCOT Grid to stabilize after a sudden loss of generation is dependent on the sufficiency of the system’s primary frequency response.  Resources providing primary frequency response must be able to provide continuous full proportional response against the frequency deviation and contribute to ERCOT’s meeting it’s FRO as established by the NERC. On January 16, 2014 FERC approved the BAL-003 NERC Frequency Response Standard pending few clarifications from NERC.  The BAL-003 standard sets a Frequency Response Obligation (FRO) for each BA and based on this standard the requirement for ERCOT is 413 MW/0.1 Hz.  The necessity of a separate PFR Down service will require further discussions.

Figure 1

Protocol Definition for Primary Frequency Response (PFR) Service –Concept Level – Consensus acceptance requested prior to Protocol Language development: Primary Frequency Response (PFR): The immediate proportional increase or decrease in real power output provided by a Resource and the natural real power dampening response provided by Load in response to system frequency deviations. This response is in the direction that stabilizes frequency. In the ERCOT Interconnection the minimum amount of guaranteed cumulative PFR Service that must be self-provided by QSEs or procured by ERCOT for every Operating Hour is determined based on minimum FFR and PFR needed to avoid under-frequency firm load shedding for simultaneous loss of two largest units totaling 2750 MW.

# Governor Setting Requirement for Generation Resources

To assure system frequency stability and compliance with NERC performance criteria, all Resources with speed governors shall have their governor in-service whenever the Resource is providing energy to the ERCOT Transmission Grid and set to operate with a droop setting not to exceed 5% and a frequency response dead band of no more than +/- 0.036 Hz.

XXXX ERCOT acknowledges that governor like actions on certain generating machines (such as synchronous Generating Resources) are inherent to the design of the machine and will occur in response to frequency deviations that exceed the machines governor dead-band setting (limited by NERC Guidelines to no more than +/- 0.036 Hz).  These actions are consistent with maintaining the frequency stability of the ERCOT Interconnection and consequently, it may be appropriate to compensate these machines in some manner for their governor like control actions.  Such compensation could be awarded on the basis of the continuous nature of the governor response or limited to those governor actions occurring as the result of the occurrence of the operating event that determines the minimum guaranteed cumulative amount of PFR that must be provided in the ERCOT Interconnection. The concept of allowing such compensation and determining the price and energy quantity are not directly related to ERCOT’s Real Time reliability and NERC compliance needs.  However, ERCOT is interested in promoting the development of Resources capable of providing PFR and is consequently interested in exploring this concept with Market Participants as an incentive to such development.

Protocol Concept – Consensus acceptance requested prior to Protocol Language development: Governor The electronic, digital, or mechanical device that implements Primary Frequency Response of a Resource. Governor Dead-Band The range of deviations of system frequency (+/-) that produces no Primary Frequency Response. ERCOT will require that Resources connected to the ERCOT Transmission System and capable of providing PFR governor actions as part of their inherent design to have their governor control systems in operation at all times when they are online. ERCOT may only require specific PFR performance criteria from those Resources that are providing PFR Service as the result of QSE self-arrangement or a DAM or RT Market award.

Possible Protocol Concepts – Selection of a concept based on a consensus choice: Market Participants may wish to propose and consider the need to include protocol provisions that would allow compensation to Resources that are not included in the self-arranged or PFR award categories but that respond by design to frequency deviations and thereby contribute to maintain the steady state frequency in the ERCOT Interconnection within defined limits. To help initiate this discussion ERCOT offers the following suggestions received from various Market Participants for consideration. ERCOT at this time does not endorse any one of these particular suggestions nor suggest that these are the only possible set of possibilities available for consideration. - Option of paying for Governor Response only during certain qualified events - A hybrid approach that continuously measures Governor Response delivered using the concept of Control Performance Standard 1 (CPS1) and event based measurement using the concept of BAL-TRE-001 Regional Standard. - Resources that are not supplying the service are NOT required to reserve capacity for governor response. They have the flexibility to offer energy in the RT Market that would otherwise be withheld to meet a PFR Responsibility. If Resources believe there is additional cost due to governor movements then those cost can be reflected in the Energy Offers. This was extensively discussed at the work sessions and the general consensus was that: - All Resources that are required to have a Governor (as specified in current protocol) must have their Governor in service and must be fully frequency responsive whenever there is capacity available to either increase output or decrease output. - Resources that were awarded PFR service will receive the payment for capacity reservation. - XXXX It was also recommended that Resources that are without any PFR responsibility can widen their Governor Dead-band up to 0.036 HZ. There will not be any compensation for providing governor response. There will not be any compensation outside the payment for capacity reservation for PFR.

# Performance Measurement

Protocol Concept – Consensus acceptance requested prior to Protocol Language development: The event based performance of Resources will be measured using the concept similar to as presented in BAL-TRE-001 Standard which has been approved by FERC on January 16, 2014. ERCOT proposes to use event driven PFR measurement using the BAL-TRE-001 Standard, Requirement R9 & R10. (http://www.texasre.org/CPDL/01-BAL-001-TRE-1_12.7.12.pdf ). ERCOT had conducted a field trial from June of 2011 until May 2012 for the period of 12 months to see the performance of selected Resources against the Requirement R9 and R10. The table below summarizes the performance of Combined Cycle, Coal/Lignite and Gas Steam Resources. Generation Type; Maximum HSL Limit; Minimum HSL Limit. Combined Cycle; 24.48%; 7.34%. Coal/Lignite; 19.48%; 4.71%. Gas Steam; 20.76%; 8.29%. Any Resources that fails the BAL-TRE-001 R9 and R10 or other similar metric will be disqualified. Once disqualified resources can request for qualification pending Governor Tests and documentation. A Resource with PFR service responsibility that does not meet the minimum performance requirement will be subject to financial penalty (details to be discussed later).

# Qualification and Limit on Resources Providing PFR

## Qualification

Protocol Concept – Consensus acceptance requested prior to Protocol Language development: In qualifying and establishing limits on Resources for providing PFR, ERCOT will consider the performance abilities and limitations of the technology of each Resource seeking to qualify as a PFR provider, subject to the requirement that the cumulative action by PFR qualified Resources must meet or exceed the system response characteristic illustrated in Figure 1. Because qualification requirements for different technologies may reflect their technical capabilities and limitations, ERCOT may impose other administrative limitations (such as the total amount of capacity reservation that can be awarded to each type of Resource technology) to assure the required system response as illustrated in Figure 1 is achievable. The technology qualification and performance requirements will be described in the ERCOT Nodal Protocols as they are developed. In the interim ERCOT will continue to qualify those Generation Resource technologies currently acknowledged as capable of providing PFR Service in the current Nodal Protocols and Operating Guides. Resources seeking to qualify as a PFR AS provider must demonstrate their ability to meet the following criteria: - Automatic Proportional response must be delivered by 16 seconds (B point) from A point (see Figure 2), droop response will be calculated at 16 seconds; and - Automatic Proportional response must be sustained for an additional 30 seconds after B point, and droop response will be calculated at 46 seconds.

## Limit of on Resources Providing PFR

This methodology would provide incentives for resources to improve their droop performance to carry more PFR capacity.  Another advantage with a performance based approach is, as Resources start performing poorly, they will be limited on how much PFR they can carry hence more resources will be carrying PFR reserves, which would further improve Grid Reliability. The performance based PFR capacity limit will work as closed loop feedback to improve PFR performance. Besides the PFR capacity limit proposed above ERCOT will limit Resources from providing a large amount of PFR on a single Resource to ensure proper distribution of PFR services.  Private Use Network (PUN) with registered Resources may use the Gross HSL for qualification and establishing a limit on amount of PFR capacity that the PUN Resources can provide.  ERCOT also proposes that the limits established on the Resources be based on their capability to provide PFR.

Calculated droop =            P∗ΔHz60∗ΔMW

P - Will be equal to the HSL of the unit and will not include any Power Augmentation.

Figure 2: Resource’s Ability to Carry PFR Capacity as Percent of HSL Based on Droop Performance

Figure 3 Showing PFR performance measurements for BAL-TRE-001 Standard

(P or HSL = 605 MW)

Table 1

Table 1 shows and example calculated droop performance based on the equation below. The 5.10 % droop performance means unit will be able to provide 118.5 MW or 19.5 9% of HSL, whichever is minimum.

Protocol Concept – Consensus acceptance requested prior to Protocol Language development: Once the PFR market is established, ERCOT will limit the PFR capacity reservation award to individual Resources based on the Median of their actual performance during past 6 events. ERCOT will calculate the MW/0.1 Hz response during these events and calculate Resource’s capability for 1% or 0.6 Hz change in frequency. If a new or previously disqualified Resource with appropriate droop setting seeks PFR qualification, ERCOT will limit the PFR capacity reservation to no more than 20% of the Resource’s Frequency Responsive HSL. Private Use Network (PUN) with registered Resources may use the Gross HSL for qualification and establishing a limit on amount of PFR capacity that the PUN Resources can provide. This is the amount of MW that can respond during a frequency event. ERCOT also proposes that the limits established on the Resources be based on their capability to provide PFR.

# Methodology to Determine Requirement for PFR service

ERCOT as the system Reliability Coordinator will determine the amount of governor capability that must be available in each hour of the Operating Day to assure a system response characteristic as illustrated in Figure 1.   ERCOT will conduct series of dynamic studies to quantify the amount of PFR needed under various system conditions. The results of these studies together with applicable safety margins and amount of FFR procured will determine how much PFR is needed for each hour of the Operating Day. ERCOT will procure at a minimum, full  amount of combined PFR and FFR needed to avoid firm  load shedding for simultaneous loss of two largest units totaling 2750 MW.

ERCOT had performed dynamic simulation studies in 2011 to study the minimum quantities of Load Response (set at 59.70 Hz triggered by UFR) and Governor Response needed to protect under-frequency load shed at 59.30 Hz for a loss of two largest units totaling 2750 MW.  The results indicate the need of 2,800 MW (up to 50% can be provided by LRs) is required for the studied high wind low load system condition.  Total load in the case was 28,400 MW including 5000 MW of PUN and 7,400 MW of wind generation.

ERCOT Fast Frequency Response

Working Document – 5-6-14

# Definition of FFR Service

Protocol Definition for Fast Frequency Response (FFR) Service –Concept Level – Consensus acceptance requested prior to Protocol Language development: Fast Frequency Response (FFR): A response from a resource that is automatically self-deployed and provides a full response within 30 cycles after frequency meets or drops below a preset threshold. FFR may also be manually deployed and full response must be provided within 10 minutes. FFR Resources based on their sustainability and ability to restore may participate in sub-group FFR1 or FFR2. A resource providing FFR1 must be able to sustain a full response for maximum of 10 minutes after being deployed manually or by reaching the preset threshold, the FFR1 resource must respond to an ERCOT recall instruction within XXX minutes and should fully restore (be able to perform the service) within 10 minutes of receiving ERCOT’s recall instruction or continuous 10 minutes of deployment, whichever comes first. If a resource larger than 200 MW self recalls at the end of the required 10 minute deployment then it shall ramp no faster than 20% of its peak deployed capacity per minute A resource providing FFR2 must be able to sustain a full response until ERCOT issues a recall instruction or the resource no longer has a responsibility to provide the service, whichever comes first. The resource must be able to fully restore its FFR2 responsibility within 90 minutes after receiving ERCOT’s recall instruction. In the ERCOT Interconnection, the minimum amount of guaranteed cumulative FFR Service that must be self-provided by QSEs or procured by ERCOT for every Operating Hour is determined based on minimum FFR and PFR needed to avoid under-frequency firm load shedding for simultaneous loss of two largest units totaling 2750 MW.

Definition of NERC Contingency Reserve

The provision of capacity deployed by the Balancing Authority to meet the Disturbance Control Standard (DCS) and other NERC and Regional Reliability Organization contingency requirements.

Per BAL-002-01.

R6. A Balancing Authority or Reserve Sharing Group shall fully restore its Contingency Reserves within the Contingency Reserve Restoration Period for its Interconnection.

R6.1. The Contingency Reserve Restoration Period begins at the end of the Disturbance Recovery Period.

R6.2. The default Contingency Reserve Restoration Period is 90 minutes.

Note: The term “Contingency Reserves” as used by NERC in the above includes the capacity reserves for FFR, PFR, Regulation and Contingency Reserve Services as described by ERCOT in the new Ancillary Services product set

Multiple Contingencies within the Contingency Reserve Restoration Period

Additional Reportable Disturbances that occur after the end of the Disturbance Recovery Period but before the end of the Contingency Reserve Restoration Period shall be reported and included in the compliance evaluation. However, the Balancing Authority or Reserve Sharing Group can request a waiver from the Resources Subcommittee for the event if the contingency reserves were rendered inadequate by prior contingencies and a good faith effort to replace contingency reserve can be shown.

# Need for FFR Service

Primary Frequency Response is achieved through Governor or Governor-like action that is immediate and proportional to the frequency deviation; this response is generally delivered completely within 12 seconds to 14 seconds.  Fast Frequency Response (FFR) provides a full MW response within 30 cycles, slowing the frequency decay and allowing sufficient time for PFR-capable resources to respond.  The benefits and needs of FFR are:

### Increasing the time from point A (pre-disturbance, normal system frequency) to point C (frequency nadir/peak after a sudden power imbalance), shown in Figure 2, allowing PFR resources to respond and assist in arresting frequency decay.

### Raising the level of the frequency nadir to reduce the risk of frequency reaching or dropping below the first tier of under frequency load shedding, which is the backstop for the simultaneous loss of the system’s two largest units, totaling 2750 MW.

During periods with low inertia, in the absence of FFR Service, much higher PFR capacity reservation would be needed to ensure that sufficient response capability is available to arrest sudden frequency decay in the event of generation losses.

The system need for Fast Frequency Response is that the resource fully responds before the C point, sustains its response long enough in order for full deployment of Contingency Reserve Service and restores quickly after the recall.  Resources that can provide either FFR1 or FFR2 are beneficial to ERCOT and therefore it is acceptable to allow both types of Resources to provide Fast Frequency Response.

FFR1 has maximum obligation of 10 minutes and must restore within 10 minutes following ERCOT recall instruction which means FFR1 will respond in 30 cycles and will restore itself in a short duration and be ready for the next event. FFR1 will also be at higher frequency set-point than FFR2 and therefore will be expected to respond to more events than FFR2.

On the other hand FFR2 is suitable for the resources that can be deployed for longer period but cannot be restored quickly like FFR1. During manual deployment FFR2 will be beneficial due to its ability to remain deployed for longer period.

Figure 2	Typical frequency response following a generator trip.

# Deployment and Recall Requirement for FFR

A Resource providing FFR shall monitor the system frequency and must deploy under the following conditions: - Automatically self-deploy and provide a full response within 30 cycles after frequency meets or drops below a preset threshold initially set to 59.9 Hz. - Capable of manual deployment upon ERCOT instruction with full response provided within 10 minutes ERCOT will use the current Responsive Reserve recall threshold of 59.97 Hz (for more than 1 minute) to recall FFR1 and FFR2 resources after automatic deployments. During the manual deployments FFR1 can restore after maximum deployment period of 10 minutes and FFR2 can only restore following a recall instruction by ERCOT. The maximum amount of FFR1 to be procured will be selected such that frequency will not got above 60.1 Hz when deployed.

### Discussion:

### The initiation setting of the under-frequency relay shall not be any lower than 59.7 Hz;

### The under-frequency relay must have a delay of no more than 20 cycles (or 0.33 seconds for relays that do not count cycles). Total time from the time frequency first decays to a value low enough to initiate action of the under frequency relay(s) to the time Load is interrupted should be no more than 30 cycles, including all relay and breaker operating times;

### When FFR is automatically deployed, ERCOT will deploy CR to restore FFR.

### ERCOT will issue the FFR recall instruction when the system frequency is equal to or above 59.97 Hz for more than 1 minute and the Contingency Reserve Capacity (NERC defined) has been restored to an acceptable level.

# Qualification and Performance Measurement on Resources Providing FFR

## Qualification

A resource to be qualified for FFR services needs to meet the followings: - Shall independently detect and record system frequency with an accuracy of at least one mHz. - Shall automatically self-deploy the service within 30 cycles through an actual or pseudo frequency event. - Shall be capable of manual deployment within 10 minutes following ERCOT’s instruction. - Shall be capable of sustaining the full deployment for at least 10 minutes. - The maximum capacity for a resource to participate in FFR shall be equal to or less than the approved capacity in the qualification test.

## Performance Measurement

A resource providing FFR service is required to meet the performance requirements in the following: - When deployed the Resource must provide a minimum of 95% or maximum of 150% of the awarded FFR Responsibility. - When automatically deployed the Resource must provide full response within 30 cycles once reaching the defined frequency threshold. - When manually deployed by ERCOT the Resource must provide full response within 10 minutes once receiving ERCOT’s deployment instruction. - A QSE shall fully restore its FFR1 responsibility within 10 minutes after receiving ERCOT’s recall instruction. A QSE shall fully restore its FFR2 responsibility within 90 minutes after receiving ERCOT’s recall instruction.

# Methodology to Determine Requirement for FFR service

# Similar to Primary Frequency Response, ERCOT as the system Reliability Coordinator will determine the amount of FFR that needs to be procured in each hour of the Operating Day to assure an acceptable system frequency response.  ERCOT will conduct series of dynamic studies to quantify the amount of FFR and PFR needed under various system conditions.  The results of these studies together with applicable safety margins and amount of FFR procured will determine how much PFR is needed for each hour of the Operating Day.

# Work session and workshop discussions comments

(1/31/2014 work session)

- Should ERCOT consider FFR-DOWN?

No, but should consider the FFR-DOWN software implementation.

(General consensus is to defer this item for later)

- Should ERCOT consider multiple frequency thresholds for FFR deployment?

No. ? (General consensus was that from Reliability perspective it makes sense but the market design gets really complicated, it was suggested to defer this for future until we see more compelling reliability reason. Some of this multiple frequency threshold is already happening today.)

- What is an appropriate sustained response period for FFR? (The general consensus was that it’s not full hour but much shorter than full hour, it was suggested to align this with some existing NERC standard. ERCOT suggests a 10 minute sustained minimum period. This would allow sufficient time for the impact of the SCED dispatch of Contingency Reserve (CR) to be realized.

- What is an appropriate restoration period after receiving ERCOT’s recall signal?

FFR deployment sustained response for up to 10 minutes and should restore the responsibility within 90 minutes.

- What issues are associated with varying hourly FFR requirements?

Have further discussion after understanding the assessment results. (The general consensus was that month ahead determination of minimum requirements is sufficient advance notice. ERCOT’s draft proposal to produce indicative yearly minimum requirements based on offline studies was supported by Market Participants)

- Should a resource participating in FFR be required to provide ERCOT with high resolution measurement data for both qualification and performance evaluation?

Require Resources to provide high resolution records after receiving ERCOT’s request.  No need to provide real time data or additional meter point to SCADA.

(2/21/2014 work session, 2/26/2014 workshop)

- Need to discuss the FFR restoration time and provide historical LR’s deployment and restoration information.

ERCOT will provide an update in the working session on 2/28/2014.

- Clarify the FFR manual deployment triggers.

In progress, will provide updates in the working session in March, 2014.

- Re-evaluate the FFR measurement recorder needs.

ERCOT will provide an update in the work session on 2/28/2014 and revise the FFR working document language after the work session.

- Clarification of the qualification of FFR.

ERCOT will provide an update in the work session on 2/28/2014 and revise the FFR working document language after the work session.

- Recommend to have resources discuss their capability, concern and challenges to participate in the FFR service in the following FAST workshop.

ERCOT will reach out to the DSWG and other WGs.

- Post redline PFR work document.

Been posted at http://www.ercot.com/calendar/2014/02/20140225-FAST

- ERCOT to provide historical frequency performance .

| Year | <59.70 HZ | <59.75 HZ | <59.80 Hz |
| --- | --- | --- | --- |
| 2008 | 0 | 1 | 4 |
| 2009 | 0 | 0 | 4 |
| 2010 | 1 | 7 | 21 |
| 2011 | 0 | 6 | 18 |
| 2012 | 0 | 6 | 16 |
| 2013* | 0 | 5 | 9 |

Outline of Qualification Requirements and Event Performance Process for Fast Frequency Response Resources

Qualification Requirements:

- Complete the Resource Asset Registration process

- Provide One-Line Diagrams and Drawings

- Demonstrate the resource’s capability to meet FFR requirements.  A resource can apply one of the following approaches to demonstrate their capability.

  - Installed Under-frequency Relay and provide validated relay test sheet to ERCOT.

  - An actual test.

- Telemetry installed and tested from the QSE to ERCOT

- Successfully complete a manual deployment test defined by ERCOT

- A qualified FFR Resource needs to verify their capability to every two years.  And an actual performance can be used as demonstrate their capability and meet this biennial verification requirement.

Event Performance Process:

For a deployment event triggered by an under-frequency event

- Following an under-frequency event ERCOT will collect the following data:

  - Source information that triggered the event

  - High speed event data from the recorders at ERCOT Taylor and Bastrop facilities

  - High speed event data from Phasor Measurement Units (PMUs) available to ERCOT.

  - PI data from all FFR Resources with a responsibility during the event

- ERCOT will use high speed event data to determine if frequency threshold was reached for at least 20 cycles

- If the frequency reached the trip threshold for at least 20 cycles at all measurement locations in ERCOT, all FFR Resources with FFR responsibility are expected to be fully deployed.

    - PI data will be used to determine if the following requirements were met:

      - Did the resource deploy 95% to 150% of its responsibility?

      - Did the resource sustain 95% to 150% of its responsibility for the duration of the sustained response period?

      - Did the resource return to service by the end of the designated recovery period?

    - If any of the requirements within 2.A.i above are not met ERCOT will submit a complaint to Compliance that could lead to a potential Protocol Violation and TRE/PUCT investigation unless the QSE moved the responsibility to another qualified resource.

    - Prior to submitting a complaint to Compliance a FFR Resource will be granted an opportunity to provide site specific high speed data for consideration.

- If the frequency reached the trip threshold at some but not all of the measurement locations, ERCOT will evaluate the requirement on a zonal or regional basis.

    - ERCOT will use its professional judgment to divide the ERCOT grid into zones or regions for performance analysis purposes.

    - If ERCOT decides within the zone or region that the frequency reached the trip threshold for at least 20 cycles then all FFR resources within that zone or region will be expected to deploy FFR responsibility.

    - PI data will be used to determine if the following requirements were met:

      - Did the resource deploy 95% to 150% of its responsibility?

      - Did the resource sustain 95% to 150% of its responsibility for the duration of the sustained response period?

      - Did the resource return to service by the end of the designated recovery period?

    - If any of the requirements within 2.B.iv. above are not met ERCOT will submit a complaint to Compliance that could lead to a potential Protocol Violation and TRE/PUCT investigation.

    - Prior to submitting a complaint to Compliance a FFR Resource will be granted an opportunity to provide site specific high speed data further analysis.

For a deployment event triggered by Verbal Dispatch Instruction

- Following a deployment from a verbal dispatch instruction ERCOT will collect the following data:

  - Voice recording of the dispatch instruction to document the time of the instruction. The official start of the ramp period for the FFR deployment is the end of the ERCOT operator’s acknowledgement that the read back of the instruction was correct.

  - PI data from all FFR Resources with a responsibility during the event

- PI data is analyzed to determine the following requirements were met:

  - Did the resource deploy 95% to 150% of its responsibility by the end of the ramp period?

  - Did the resource sustain 95% to 150% of its responsibility for the duration of the sustained response period?

  - Did the resource return to service by the end of the designated recovery period?

- This analysis is performed at both the QSE portfolio level and individual resource level. If the portfolio meets these requirements the QSE will be deemed to have met its responsibility for the event.

- If any of the requirements within #2 above are not met at the QSE’s portfolio level ERCOT will submit a complaint to ERCOT Compliance that could lead to a potential Protocol Violation and TRE/PUCT investigation. Individual FFR resources will also be included in the complaint only when the portfolio fails to meet any of the above noted requirements.

ERCOT Contingency Reserve Service

Working Document – Work Session (5-2-2014):

# Definition of CR Service

Protocol Definition for Contingency Reserve (CR) Service –Concept Level – Consensus (99%, 03212014) acceptance requested prior to Protocol Language development: Contingency Reserve (CR) Service: An Ancillary Service provided by Generation Resources that can be synchronized and ramped to a specified output level within 10 minutes and Load Resources that can provide demand response within 10 minutes, and that can sustain the specified response (CR responsibility) for at least one hour. In the ERCOT Interconnection, the minimum amount of guaranteed cumulative CR Service that must be self-arranged by QSEs or procured by ERCOT for every Operating Hour will be determined based on minimum CR need to recover Area Control Error (ACE) to a pre-disturbance level within 15 minutes following the Most Severe Single Contingency (currently 1375 MW) and 10-min net load ramp consideration, whichever is higher.

# Needs of CR Service

Following large generator trip FFR and PFR will be deployed (as discussed in respective working documents). FFR will facilitate arresting frequency decay (point C, Figure 1), PFR will stabilize frequency (point B, Figure 1) at certain level, normally lower than pre-disturbance frequency. In the attempt to recover frequency to a pre-disturbance level, available Regulation Reserves will be deployed.  However, the purpose of Regulation Reserve is to keep Area Control Error within a narrow dead band in normal operation (to balance 5-min net load variability).  Regulation Reserve therefore is not dimensioned for generation trip events and might also be fully deployed at the time when generation trip event happens.

Contingency Reserve is needed to restore frequency within defined limits following a large generator trip event. The Contingency Reserve may also be used to cover for large net load ramps.

NERC Standard BAL-002-1 Disturbance Control Standard (DCS) requires ERCOT to carry enough reserve to recover its ACE to pre-disturbance level within 15 minutes, after a Reportable Disturbance.

ERCOT will determine minimum amount of CR needed to ensure compliance with NERC DCS standard following the Most Severe Single Contingency (currently 1375 MW).

To ensure ERCOT can meet NERC DCS standard, the CR must be fully deliverable within 10 minutes so that Frequency can be restored to the pre-disturbance level within 15 minutes.

Manual deployment of CR may also be needed during scarcity hours and severe weather events to resolve capacity insufficiency.

Figure 3

Definition of NERC Contingency Reserve

The provision of capacity deployed by the Balancing Authority to meet the Disturbance Control Standard (DCS) and other NERC and Regional Reliability Organization contingency requirements.

Per BAL-002-01.

R6. A Balancing Authority or Reserve Sharing Group shall fully restore its Contingency Reserves within the Contingency Reserve Restoration Period for its Interconnection.

R6.1. The Contingency Reserve Restoration Period begins at the end of the Disturbance Recovery Period.

R6.2. The default Contingency Reserve Restoration Period is 90 minutes.

Note: The term “Contingency Reserves” as used by NERC in the above includes the capacity reserves for FFR, PFR, Regulation and Contingency Reserve Services as described by ERCOT in the new Ancillary Services product set

# Deployment, Sustain and Recall Requirements for CR

ERCOT proposes to distinguish between two types of CR: (99%,03212014) - CR1 – Contingency Reserve provided by Resources available for deployment in SCED, e.g. Generation Resources and Controllable Load Resources (CLR); - CR2 – Contingency Reserve provided by Resources not available for deployment in SCED, e.g. non-controllable “blocky” Load Resources; It is proposed that CR1 and CR2 are cleared together with total procured CR=CR1+CR2. The distinction between CR1 and CR2 is purely based on capability of Resources to be deployed through SCED. Note: Resource Adequacy Task Force is currently discussing proposals to mitigate price impact from deployment of “blocky” Resources. Same principles will apply to “blocky” CR. Requirements for Resources providing CR1 Capacity of Resources with CR1 responsibility will automatically be released to SCED once system frequency drops below 59.91 Hz or manual deployment. ERCOT shall use SCED to determine the amount of energy to be dispatched from CR1 Resources once the Resource status is On-Line. Off-Line Generation Resources providing CR1 (XXXXX Resource Status) are required to provide an Energy Offer Curve for use by SCED. A Resource providing CR1 shall telemeter their ramp-rates such that SCED can dispatch the full Resource CR1 responsibility within 10 minutes if needed. A Resource providing CR1 shall be capable of sustaining its full response for as long as it has responsibility to provide this service. CR1 capacity will be recalled once frequency and PRC has reached stable threshold. Once CR1 capacity is recalled, CR1 resources will update their schedules, SCED will dispatch generating resources carrying CR1 to their HASL through base point instructions. A CR1 Dispatch Instruction from ERCOT must respect the minimum runtime of a Resource. After the recall of a CR1 Dispatch Instruction, any Generation Resource previously Off-Line providing CR1 is allowed to remain On-Line for 30 minutes following the recall. During that time period, the On-Line Generation Resource is treated as if the CR1 is being provided. Requirements for Resources providing CR2: Non-controllable Resources will be manually deployed by ERCOT outside of SCED. CR2 will be deployed only if deployment of CR1 and SR1are not sufficient and more resources are needed to mitigate system events or meet regulatory standards. ERCOT will develop a set of conditions to govern manual deployment of CR2 based on system outlook and PRC considerations to meet NERC DCS standard. Manual deployment of CR2 will take place prior to manual deployment of FFR2 and after manual deployment of SR2 unless CR2 deployment is necessary for compliance with NERC DCS. In this case CR2 will be deployed before SR2. Resources providing CR2 shall be capable of reaching its full CR2 responsibility within 10 minutes following manual deployment instruction. A Resource providing CR2 shall be capable of sustaining its full response for as long as it has responsibility to provide this service. CR2 deployment will be recalled once frequency and PRC have reached a pre-set acceptable threshold. Once recalled, Resource providing CR2 should be capable of restoring its CR2 responsibility, within 180 minutes for it to be qualified as CR2.

# Performance Measurement

Resources providing CR1 will be subject to disqualification in addition to SCED base point deviation charges for failure to follow SCED base point

Resources providing CR1 should deploy at least 95% of the responsibility within 10 minutes after receiving corresponding SCED base point instructions.

Resources providing CR2 should deploy at least 95% of the responsibility within 10 minutes after receiving corresponding manual deployment instructions.

# Qualification of Resources Providing CR

Protocol Concept – Consensus acceptance requested prior to Protocol Language development: (100%, 03212014) Resources providing CR should be qualified up to MW value they are able to ramp to within 10 minutes from the time of deployment. Resources providing CR1 should be capable of following SCED dispatch and must telemeter their ramp-rates such that SCED can dispatch Resources full CR1 responsibility within 10 minutes. Resources providing CR2 must provide a telemetered output signal and should be capable of following ERCOT instructions and deploy the full responsibility within 10 minutes. Failure to meet any requirement stated above would result in disqualification from providing CR. Once disqualified, the Resources can request requalification any time after 30 days. Resources providing CR must be able to deliver and sustain the reserve deployments for the full hour they are carrying that responsibility.

# Methodology to Determine Requirement for CR service

ERCOT as the system Reliability Coordinator will determine the minimum amount of CR that must be available in each hour of the Operating Day to ensure compliance with NERC BAL-002-01 standard and cover for large 10-min net load ramps. ERCOT will determine maximum share of CR that can be provided between CR1 and CR2.

ERCOT will conduct analysis and studies to confirm sufficiency of CR, determined as described above, under various system conditions.

ERCOT Supplemental Reserve Service

Working Document – Work Session (3-28-2014):

# Definition of Supplemental Reserve Service

An Ancillary Service that is provided through use of Off-Line Generation Resources that can be synchronized and ramped to a specified output level within 30 minutes, or Load Resources that can provide demand response within 30 minutes, and that can sustain the specified response for at least one hour.

Supplemental Reserve (SR) Service is provided by using:

(a)	Generation Resources (SR1) that are Off-Line and capable of:

(i)	Being synchronized and ramped to a specified output level within 30 minutes; and

(ii)	Running at a specified output level for at least one hour; or

(b)	Controllable Load Resources (SR1) qualified for Dispatch by Security-Constrained Economic Dispatch (SCED) and capable of:

(i)	Ramping to an ERCOT-instructed consumption level within 30 minutes; and

(ii)	Consuming at the ERCOT-instructed level for at least one hour.

(c)	Non-Controllable Load Resources (SR2) which are manually deployed and are capable of:

(i)	Delivering their demand response within 30 minutes; and

(ii)	Sustaining the response for at least one hour.

Concept Level – Consensus acceptance requested prior to Protocol Language development: # Definition of Supplemental Reserve Service (100% 03212014) An Ancillary Service that is provided through use of Off-Line Generation Resources that can be synchronized and ramped to a specified output level within 30 minutes, or Load Resources that can provide demand response within 30 minutes, and that can sustain the specified response for at least one hour.

# Needs of SR Service

# SR service is the reserve that is used to compensate for net load forecast error, abnormal number of unit unavailability and/or net load ramps. ERCOT may also procure additional SR capacity in anticipation of severe weather conditions. While ERCOT believes that SR Service may not ultimately be required in the long term, it may be needed during the transition. ERCOT also believes there is a value in defining the product and creating a placeholder within the ERCOT applications.

# Deployment, Sustain and Recall Requirement for SR

ERCOT proposes to distinguish between two types of SR : (98 % 03212014) - SR1 – Supplemental Reserve provided by Resources available for deployment in SCED, e.g. Generation Resources and Controllable Load Resources (CLR); - SR2 – Supplemental Reserve provided by Resources not available for deployment in SCED, e.g. non-controllable “blocky” Load Resources; It is proposed that SR1 and SR2 be cleared together with total procured SR=SR1+SR2. The distinction between SR1 and SR2 is purely based on capability of Resources to be deployed in SCED. Note: Resource Adequacy Task Force is currently discussing proposals to mitigate price impact from deployment of “blocky” Resources. Same principles will apply to “blocky” SR. Requirements for Resources providing SR1 ERCOT shall use SCED to determine the amount of energy to be dispatched from SR1 Resources. Off-Line Generation Resources providing SR (XXXXX Resource Status) are required to provide an Energy Offer Curve for use by SCED. A Resource providing SR1 shall telemeter its ramp-rates such that SCED can dispatch the full Resource SR responsibility within 30 minutes if needed. A Resource providing SR1 shall be capable of sustaining its full response for as long as it has responsibility to provide this service. SCED base point instructions will determine dispatch instruction for Generating Resources providing SR1. SR deployment can be recalled once frequency and PRC has reached stable threshold and reserve outlook appears stable. Once SR1 capacity is recalled, SR1 resources will update their schedules, SCED will dispatch generating resources carrying SR1 to their HASL through base point instructions. A SR1 Dispatch Instruction from ERCOT must respect the minimum runtime of a Resource. After the recall of a SR1 Dispatch Instruction, any Generation Resource previously Off-Line providing SR1 is allowed to remain On-Line for 30 minutes following the recall. During that time period, the On-Line Generation Resource is treated as if the SR1 is being provided. Requirements for Resources providing SR2 Resources providing SR2 shall be manually deployed by ERCOT outside of SCED. SR2 will be deployed only if deployment of CR1 and SR1 are not sufficient and more resources are needed to mitigate system events or meet regulatory standards. . ERCOT will develop a set of conditions to govern manual deployment of SR2 based on system outlook and PRC considerations to meet NERC DCS standard. Manual deployment of SR2 will take place prior to any manual deployment of FFR2 and CR2, unless CR2 deployment is necessary for compliance with NERC DCS. In this case CR2 will be deployed before SR2. On receipt of a deployment instruction, Resources providing SR2 must, at a minimum, provide the requested deployment energy within 30 minutes of the Dispatch Instruction. Within 20 minutes after receipt of the deployment instruction, the QSE shall reduce the SR Ancillary Service Schedule by the amount of the Load Resource deployment. A Load Resource consisting of an aggregation of Loads must comply with all requirements in the document titled “Requirements for Aggregate Load Resource Participation in the ERCOT Markets.” A Resource providing SR2 shall be capable of sustaining its full response for as long as it has responsibility to provide this service. SR capacity will be recalled once frequency and PRC has reached stable threshold. Once recalled, Resource providing SR2 should be capable of restoring its SR2 responsibility, within 180 minutes for it to be qualified as SR2. .

# SR Capacity Monitoring and Performance Measurement

ERCOT shall continuously monitor the capacity of each Resource to provide SR. ERCOT shall consider for each Resource providing SR capacity, the actual generation, or Load, the Ancillary Service Schedule for SR, the HSL/Maximum Power Consumption (MPC), the LSL/Low Power Consumption (LPC), ramp rates, and any other commitments of Ancillary Service capacity.

# Qualification of Resources Providing SR

Protocol Concept – Consensus acceptance requested prior to Protocol Language development ( 99% 03212014) Each Resource providing SR must be capable of being synchronized and ramped to its Ancillary Service Schedule for SR within 30 minutes. SR1 must be provided from Off-Line Generation Resource or Controllable Load Resources capacity that can ramp within 30 minutes. SR2 is provided from Load Resources capable of providing demand response within 30 minutes. SR must be provided from capacity that is not fulfilling any other energy or capacity commitment. A Load Resource providing SR must provide a telemetered output signal. QSEs using a Load Resource to provide SR must be capable of responding to ERCOT Dispatch Instructions. Load Resources should be qualified for SR2 up to the MW value by which they are able to decrease (or interrupt) their power consumption within 30-minutes from the time of deployment and remain at the specified output level (interrupted) for at least one hour. Generating Resources providing SR must telemeter their ramp-rates such that SCED can dispatch Resources’ full SR responsibility within 30 minutes. Failure to meet any requirement stated above would result in disqualification from providing SR. Once disqualified, the Resources can request requalification any time after 30 days. Resources providing SR must be able to deliver and sustain the reserve deployments for the all hours that it is carrying SR responsibility.

# Methodology to Determine Requirement for SR service

ERCOT as the system Reliability Coordinator will determine the amount of SR that must be available in each hour of the Operating Day. Since SR is a reserve used to compensate for net load forecast error, abnormal number of unit unavailability and/or net load ramps; ERCOT will conduct analyses and studies to confirm sufficiency of SR, determined as described above, under various system conditions.

ERCOT Regulating Reserve Service

Working Document – 5-6-14

# Definition of Regulating Reserve Service

Protocol Definition for Regulating Reserve Service –Concept Level acceptance requested prior to Protocol Language development– Consensus (51% 04042014) Regulating Reserve Service: An Ancillary Service that consists of either Regulation Down Service (Reg-Down) or Regulation Up Service (Reg-Up). Fast Responding Regulation Service (FRRS) A subset of Regulation Service that consists of either Fast Responding Regulation Down Service (FRRS-Down) or Fast Responding Regulation Up Service (FRRS-Up). Except where otherwise specified, all requirements that apply to Regulation Service also apply to FRRS. Regulation Down Service (Reg-Down) An Ancillary Service that provides capacity that can start responding to signals from ERCOT within five seconds . Such capacity is the amount available below any Base Point but above the LSL of a Generation Resource and may be called on to change output as necessary throughout the range of capacity available to maintain proper system frequency. A Load Resource providing Reg-Down must be able to increase and decrease Load as deployed within its Ancillary Service Schedule for Reg-Down below the Load Resource’s MPC limit. Fast Responding Regulation Down Service (FRRS-Down) A subset of Reg-Down in which the participating Resource provides Reg-Down capacity to ERCOT within 1 second of either its receipt of an ERCOT Dispatch Instruction or its detection of a trigger frequency independent of an ERCOT Dispatch Instruction. Except where otherwise specified, all requirements that apply to Reg-Down also apply to FRRS-Down. Regulation Up Service (Reg-Up) An Ancillary Service that provides capacity that can start responding to signals from ERCOT within five seconds. Such capacity is the amount available above any Base Point but below the HSL of a Generation Resource and may be called on to change output as necessary throughout the range of capacity available to maintain proper system frequency. A Load Resource providing Reg-Up must be able to increase and decrease Load as deployed within its Ancillary Service Schedule for Reg-Up above the Load Resource’s LPC limit. Fast Responding Regulation Up Service (FRRS-Up) A subset of Reg-Up in which the participating Resource provides Reg-Up capacity to ERCOT within 1 second of either its receipt of an ERCOT Dispatch Instruction or its detection of a trigger frequency independent of an ERCOT Dispatch Instruction. Except where otherwise specified, all requirements that apply to Reg-Up also apply to FRRS-Up.

## Need for Regulating Reserve Service

Protocol Definition for Regulating Reserve Service –Concept Level acceptance requested prior to Protocol Language development– Consensus (XXX) ERCOT generation is dispatched through Security Constrained Economic Dispatch (SCED) to balance the generation and demand. The power imbalance between each SCED interval will cause frequency deviation that requires regulating reserve to compensate. RR service will not substantially change from where it is today. The proposed changes are discussed in next section. ERCOT based on the feedback from FAST work-session also proposes that FAST team explore the option of running SCED every 3 minutes to efficiently meet the net load variation and reduce overall regulation need. ERCOT also received another suggestion, which was to run SCED automatically whenever 70% of regulation is deployed. Definition of NERC Regulating Reserve An amount of reserve responsive to Automatic Generation Control, which is sufficient to provide normal regulating margin. Per BAL-005-0.1b. R2. Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. (NERC BAL-001 Standard) Deployment to resources via QSE-keep same, may need different performance mechanism. Pay for performance proposed by 0404 Work-session participants and Pay for performance will be discussed in future work-sessions.

# Deployment, Sustain and Recall Requirements for Regulating Reserve

Protocol Definition for Regulating Reserve Service –Concept Level acceptance requested prior to Protocol Language development– Consensus (XXX) Load Frequency Control (LFC) The deployment of those Resources that are providing Regulation Service to ensure that system frequency is maintained within predetermined limits and the deployment of those Resources providing CR1 when necessary to backup regulation. Resources must be able to fully sustain regulation deployments for the entire duration they have responsibility and are deployed by LFC. They should also be able to follow the recall instructions. Section 6.5.7.6.1 LFC Process Description of Nodal Protocol provides additional details on deployment of regulation service through LFC. - Regulation Up (Reg-Up) Service is a service that provides capacity that can respond to signals from ERCOT within five seconds. . The amount of Reg-Up capacity is the amount of capacity available from a Resource that may be called on to change output as necessary to maintain proper system frequency. A Generation Resource providing Reg-Up must be able to increase energy output when deployed and decrease energy output when recalled. A Load Resource providing Reg-Up must be able to decrease Load when deployed and increase Load when recalled. - Fast-Responding Regulation Service Up (FRRS-Up) is a subset of Reg-Up Service in which the participating Resource provides Reg-Up capacity to ERCOT within one second of its receipt of an ERCOT Dispatch Instruction or within 30 cycles of the detection of a trigger frequency independent of an ERCOT Dispatch Instruction. ERCOT dispatches Reg-Up by a Load Frequency Control (LFC) signal. The LFC signal for FRRS-Up is separate from the LFC signal for other Reg-Up. - Regulation Down (Reg-Down) Service is a service that provides capacity that can respond to signals from ERCOT within five seconds. The amount of Reg-Down capacity is the amount of capacity available from a Resource that may be called on to change output as necessary to maintain proper system frequency. A Generation Resource providing Reg-Down must be able to decrease energy output when deployed and increase energy output when recalled. A Load Resource providing Reg-Down must be able to increase Load when deployed and decrease Load when recalled. - Fast-Responding Regulation Service Down (FRRS-Down) is a subset of Reg-Down Service in which a participating Resource provides Reg-Down capacity to ERCOT within one second of either its receipt of an ERCOT Dispatch Instruction or the detection of a trigger frequency independent of an ERCOT Dispatch Instruction. ERCOT dispatches Reg-Down by an LFC signal. The LFC signal for FRRS-Down is separate from the LFC signal for other Reg-Down.

- Performance Measurement

- Protocol Definition for Regulating Reserve Service –Concept Level acceptance requested prior to Protocol Language development– Consensus (XXX) - GREDP for Resources providing Regulation Reserve Service must be less than or equal to 5 %. (alternatively the FAST could explore Sydney’s CPS1 type metric for Resources providing Regulation Services) -put MW limit as tolerance - FRRS Resources must demonstrate their full responsibility for sudden low frequency event. Failure to respond to more than X event each month will result in disqualification. (similar to FFR) - Tighter performance metric - verify GREDP metric% and MW limit (8.1.1.4.1 (7) “A Generation Resource or DSR Portfolio, excluding an IRR, must have a GREDP less than the greater of X% or Y MW for 85% of the five-minute clock intervals in the month during which GREDP was calculated.”) - Analyze current providers with tighter metric

- Limits on Resources providing Regulation Service

Protocol Definition for Regulating Reserve Service –Concept Level acceptance requested prior to Protocol Language development– Consensus (XXX) Since Regulating Reserve is intended to balance the system between five-minute SCED intervals, their deployment and recall capability needs to be consistent. If same Resources are carrying both Regulation-up and Regulation-Down, then Regulation-up has to be fully recalled before Regulation down can be deployed. When Regulation-Up is being recalled, it does act like regulation down so the ramp rate has to be consistent. - Resources providing Regulation and being dispatched by SCED should be limited to min(NURR,NDRR)*5*0.70, where NURR and NDRR are Normal-Up Ramp Rate and Normal-Down Ramp Rate - Resources providing Regulation and not being dispatched by SCED should be limited to min(NURR,NDRR)*5, where NURR and NDRR are Normal-Up Ramp Rate and Normal-Down Ramp Rate. ERCOT will describe how the signal is calculated and deployed so as not to over respond and cause other issues - The factor of 0.7 is included to prevent SCED from using up the entire ramping capability on units carrying RR, thus leaving 70% ramping capability to respond if Regulating Reserve deployment is needed. - ERCOT proposes that a single Resource be not allowed to carry more than 25% of total regulation requirement for that particular hour. - Resources providing regulating reserve should be able to closely follow ERCOT Load Frequency Control (LFC) signal for Regulation to be effective

# Qualification of Resources Providing Regulation Service

Protocol Concept – Consensus acceptance requested prior to Protocol Language development: (XXXX) Regulation Service Qualification - A QSE control system must be capable of receiving Regulation Up Service (Reg-Up) and Regulation Down Service (Reg-Down) control signals from ERCOT’s Load Frequency Control (LFC) system, and of directing its Resources to respond to the control signals, in an upward and downward direction to balance Real-Time Demand and Resources. A QSE providing Reg-Up or Reg-Down shall provide communications equipment to receive telemetered control deployments of power from ERCOT. - A QSE shall demonstrate to ERCOT that they have the ability to switch control to constant frequency operation as specified in the Operating Guides. ERCOT’s direction to the QSE to operate on constant frequency will be considered a Dispatch Instruction. - Resources shall be qualified to provide Regulation Service up to the amount successfully tested during the qualification test. - A Resource providing Fast Responding Regulation Service (FRRS) shall be capable of independently detecting and recording system frequency with an accuracy of at least one mHz and a resolution of no less than 32 samples per second. The Resource shall also be capable of measuring and recording MW output with a resolution of no less than 32 samples per second. FRRS Resources will be required to demonstrate that they can deploy within 60 cycles of either (1) receipt of a deployment signal from ERCOT or (2) a deviation of frequency in excess of +/-.09Hz (or other automatic deployment threshold established by ERCOT) from 60 Hz. The Resource will be required to sustain the deployment for a minimum of 8 minutes at a minimum level of 95% and a maximum level of 110% of the proposed maximum capacity obligation. ERCOT will use the Resource’s high-resolution recorded frequency and MW output data to determine whether the Resource met its performance obligations during the test. A Reg-Up and Reg-Down qualification test for each Resource is conducted during a continuous 60-minute period agreed on in advance by the QSE and ERCOT. QSEs may qualify a Resource to provide Reg-Up or Reg-Down, or both, in separate testing (additional details provided in 8.1.1.2.1.1 Regulation Service Qualification of nodal protocol).

# Methodology to Determine Requirement for Regulation service

ERCOT as the system Reliability Coordinator will determine the minimum amount of Regulating Reserve that must be available in each hour of the Operating Day to meet the NERC Control Performance Standard (CPS1). ERCOT will use 5-minute net load variability and short-term load forecast error for identifying amount of regulation needed for each hour.  ERCOT will limit total Regulation Service that can come from Resources providing FRRS to X% of total system wide regulation requirement.

- Criteria for CAP to be part of the AS Methodology document.

Procurement and pricing of the proposed future set of Ancillary Services – Working Document (5/6/2014)

Revisions Description:

5/6/2014:

- Added to the Assumptions section, two items that are NOT being considered at present:

  - Pay for performance

  - Real-Time energy and AS co-optimization

- Removed sentence that implied that Load Resource (UFR-TYPE) qualified for FFR1 are not eligible to provide other AS. A Resource can provide any Ancillary Service that it has been qualified for

- MCPC for FFR1 & FFR2 is capped at VOLL

- Changed formatting of document orientation to portrait

  - Split the AS Plan table into three tables for better readability in portrait mode

  - Minor format changes

5/2/2014:

- Added RegUp, FRRS-Up, RegDn, FRRS-Dn Ancillary Services. This changed the following sections:

  - Set of Constraints for AS procurement

  - AS Plan

  - Resource Limits

  - AS MCPCs

- Other edits for clarification

  - Added description of high level rules for self-arrangement of AS in the table of constraints for AS procurement

4/25/2014:

- Modified the consensus item questions and recorded the consensus from the 4/18/2014 FAST work session meeting

  - Modified constraint for procurement of CR by removing term for contribution of FFR2 to CR.

  - Crossed out all MCPC pricing options except for Option 1 for FFR1, FFR2,  & CR2 – based on answer to question 1 in list of consensus items

- Corrected the label for the ratio of FFR/PFR ratio to PFR/FFR i.e. this ratio defines how many MW of PFR is equivalent to 1 MW of FFR

4/11/2014:

- Incorporated the ratio that equivalences 1 MW of FFR with R MW of PFR. This change removed the minimum FFR procurement constraint – impacts constraint table and AS MCPCs. This also resulted in modifications to the handling of DAM AS insufficiency process

- Section on Transition Plan introduced

- Other edits to improve description

Assumptions:

- RATF addresses pricing impacts of “blocky” MW (Load Resource – UFR Type) deployments

  - This has direct impacts on the deployment of the proposed future AS (FFR1,FFR2,CR2,SR2)

- All AS Offer prices are greater than equal to zero. i.e. no negative offer prices for AS

- For now, SIR & EIR is out of scope as further discussions are required

- The AS obligations will be determined on a Load Ratio Share basis

- For now, incorporating ORDC into DAM is not considered

- PFR & FFR services under consideration from a market procurement perspective are “upward” services, i.e. inject energy or reduce energy consumption when deployed. From a market procurement perspective, PFR “Down” and FFR “Down” services will be discussed when there is concern of over frequency (trip of a DC tie when it is carrying significant exports). The system will be built with sufficient flexibility to accommodate future addition of these “Down” services.

- For now, pay for performance for AS is not considered

- For now, Real-Time energy and AS co-optimization is not considered

Transition Plan

The transition to the proposed future set of Ancillary Service products needs to consider the following

- Implementation: In the building of the software system, instead of replacing current AS products, add the new AS products to the set of existing AS products

  - Allows flexibility of rolling in the future AS products in phases rather than “big bang” approach

  - Allows option of rolling back if issues encountered

- Ensure sufficient advance notice to the market before “go-live”. Allow enough time for hedging/forward contracting.

Example AS Offer from Load Resource (UFR-Type)

| Capacity (MW) | FFR Offer Price ($/MW) | CR Offer Price ($/MW) | SR Offer Price ($/MW) |
| --- | --- | --- | --- |
| 100 | 5 | 3 | 2 |

Note 1: Offers are Resource specific. Offers from Resources for services they are not qualified to provide will be rejected.

Note 2: The offer submittals may not specify the subgroup of the service. The system will determine which subgroup of AS (e.g. FFR1 or FFR2, CR1 or CR2, etc.) based on the qualification status within the ERCOT registration system.

Clearing process:

- The example AS offer above is only for Resources qualified for FFR2.

- The clearing process will award only ONE type of AS to this Resource as the deployment is blocky. i.e. the AS offers in the above example are treated as mutually exclusive.

- The optimization process will attempt to maximize the revenue for this Resource for a given set of AS MCPCs as opportunity costs for the different AS products are incorporated into the AS MCPCs

  - Ongoing analysis on how to deal with the binary variables introduced (mutually exclusive AS offer modelling) so that the revenue to Resource is maximized

Note 3: For Generation Resources (or other types that can submit offers to sell energy and AS offers), the clearing process with energy and AS co-optimization, has the effect of producing  LMP (energy price) and AS MCPCs (AS prices) that will maximize the Resource  total revenue from sales of energy and Ancillary Services. This is because opportunity costs for the different products are incorporated into the prices.

For example, if a Generation Resource offers 100 MW for sale of energy and Ancillary Service(s), then the result of the clearing process will be such that the sum of the energy and AS sales (awards) will be 100 MW (no overlapping of services) and the total revenue to the Generation Resource will be maximized.

Note 4: AS offers from SCED Dispatchable Resources (Generation and Controllable Load Resources) will not be treated as mutually exclusive. i.e. for the example AS Offer above, if offered from a Generation Resource or a Controllable Load Resource, then that Resource’s AS MW capacity offer can be awarded multiple AS such that the sum of the AS awards do not exceed the total MW offered for AS and the sum of the AS awards is less than or equal to HSL-LSL (or MPC-LPC for Controllable Load Resource).

AS Substitution

Current design provides the QSE submitting Resource specific AS Offers to specify for a given AS MW offer separate prices for each of the AS the Resource is qualified for (the absence of a price for a AS is taken as not offering for that AS). This allows the procurement process to optimally allocate the AS MW among the different AS. This form of AS substitution is different than the practice at other ISOs. The ERCOT form of AS substitution has the following features:

- Provides more flexibility to QSE in letting them decide which AS to offer with a price

- Does not ensure AS MCPC hierarchy where, higher quality AS are guaranteed to get a higher MCPC than lower quality AS

Procurement process

- The system wide minimum AS MW requirements on an hourly basis are posted in advance. In addition, in certain cases, the maximum AS MW allowed is also posted. The DAM 6:00 A.M. posting for AS plan will incorporate any updates to the AS MW requirements. An example is shown below:

Regulation Up and Down:

| Hour | RegUpRequirement* | FRRS-UpMaxRequirement* | RegDnRequirement* | FRRS-DnMaxRequirement* |
| --- | --- | --- | --- | --- |
| 1 | A1 | B1 | C1 | D1 |
| 2 | A2 | B2 | C2 | D2 |
| : |  |  |  |  |
| 24 | A24 | B24 | C24 | D24 |

* The AS plan requirements that can be self-arranged

Primary Frequency Response and Fast Frequency Response:

| Hour | PFRRequirement* | FFRMinRequirement* | FFRMaxRequirement | FFR1MaxRequirement* | PFR/FFR Ratio 1 MW FFR = R MW of PFR |
| --- | --- | --- | --- | --- | --- |
| 1 | X1 | Y1 | Z1 > Y1 | S1 <= Y1 | R1 |
| 2 | X2 | Y2 | Z2 > Y2 | S2 <= Y2 | R2 |
| : |  |  |  |  |  |
| 24 | X24 | Y24 | Z24 > Y24 | S24 <= Y24 | R24 |

* The AS plan requirements that can be self-arranged

Contingency Reserve and Supplemental Reserve:

| Hour | CRRequirement* | CR1MinRequirement* | SRRequirement* | SR1MinRequirement* |
| --- | --- | --- | --- | --- |
| 1 | T1 | U1 | V1 | W1 |
| 2 | T2 | U2 | V2 | W2 |
| : |  |  |  |  |
| 24 | T24 | U24 | V24 | W24 |

* The AS plan requirements that can be self-arranged

- If DAM cannot procure the required amounts of AS ( PFR or FFR or CR or SR or minimum FFR or minimum CR1 or minimum SR1), then

- Declare DAM AS insufficiency

- Re-Open DAM AS offer submittal window

- Change AS requirements plan if applicable:

  - if sufficient AS offers are not available with respect to the original AS requirements, reduce the AS requirements

    - Alternative for consideration: do not reduce AS requirements, setup AS demand curves (approved by TAC) and let the AS demand curve set the price if the rerun of DAM does not procure the AS requirements

      - Is this a better way to send appropriate price signals to the market?

- Rerun DAM

- Ultimately, if sufficient AS cannot be procured through the DAM process, then RUC process will be used to commit Resources to provide required AS.

  - Alternative for consideration: A Real-Time energy and AS co-optimization (including near term commitment) could be utilized to procure required AS.

    - Market Participants can reconfigure their portfolio closer to Real-Time

    - Resources that cannot fulfil their AS responsibilities due to Real-Time operational conditions, can buy out their AS responsibilities. (e.g. Forced Outages, Duration Limited Resources running out of stored energy, etc.)

    - Adds complexity in handling changing AS responsibilities

Other Questions

- Do we need ability to self-arrange Ancillary Services?

- What impact does the ability to negatively self-arrange Ancillary Services on the future AS procurement process?

Ancillary Service Constraints and corresponding MCPCs

This section is to start discussion on the constraints to be enforced and pricing of Ancillary Services (MCPCs). ERCOT has provided as an example, a set of constraints and the resultant MCPCs (multiple options) as a starting point for discussion.

Objective for the optimization engine is to minimize offer based costs (supply: energy & AS) minus bid based revenue (demand: energy & PTP) subject to constraints for power balance, AS procurement, transmission flow, etc. (This is the same as stating the objective to be the maximization of bid based revenue (demand: energy & PTP) minus offer based costs (supply: energy & AS). The objective for the engine is the same as what we have today in DAM.

Example Resource Limit Constraints in DAM:

Generation Resource:

LSL <= Energy + SR1 + CR1 + PFR (or FFR1) + RegUp (or FRRS-Up) <= HSL

LSL <= Energy – RegDn (or FRRS-Dn)

Controllable Load Resource:

LPC <= RegUp (or FRRS-Up) + PFR + CR1 + SR1 + RegDn (or FRRS-Dn) <= MPC

Load Resource (UFR-Type qualified for FFR2):

LPC <= SR2 <= MPC; or LPC <= CR2 <= MPC; or LPC <= FFR2 <= MPC

Load Resource (UFR-Type qualified for FFR1): LPC <= FFR1<= MPC

Note 1: Resource can only be awarded a given type of AS if they have been qualified for providing that AS.

Note 2: If applicable, there will be a limit on the maximum amount of a given type of AS that a Resource can be awarded.

Note that the Load Resources cannot submit Resource specific demand bids (bid to buy) and hence the Load Resource Limit Constraints do not have an energy consumed portion between their lower and upper limits.

- In the current ERCOT market, all demand (load) is bought at the Load Zone (except for Wholesale Load). Load Resources cannot submit Resource Specific (locational) demand bids (bid to buy energy). Load Resources can only submit Resource specific Offers to sell Ancillary Services.

- Generation Resources, however, can submit Resource specific Offers to sell energy and Ancillary Services.

- Due to the above two features of our market design, in the DAM optimization:

  - For Generation Resources, the energy and AS co-optimization process allocates the offered MW capacity (constrained between LSL and HSL) between energy and Ancillary Services taking into account opportunity costs for energy and Ancillary Services. i.e. the prices (LMP-energy and MCPC-AS) incorporate opportunity costs

  - For Load Resources, as there is no energy component (demand), the energy and AS co-optimization process only allocates the offered MW capacity considering only AS offer(s)

- If AS offers from Load Resources were cleared against the AS requirement from Load Resources, as there is no consideration of energy, then the corresponding AS MCPC will be determined solely by the marginal AS Offer from Load Resources – there is no opportunity cost for energy incorporated.

Consensus Item:

| # | Question | Comments | Consensus from 4/18/2014 FAST Work Session |
| --- | --- | --- | --- |
| 1 | Should the MCPC for FFR (FFR1 & FFR2), CR2, SR2 reflect opportunity costs for energy and other Ancillary Services? | YES- There is precedence as can be seen in setting the MCPC for RRS from Zonal and Nodal Markets YES- Liquidity concerns in terms of sufficient AS offers from Load Resources to meet FFR,CR2,SR2 are mitigated NO- These are different AS products and should be cleared against the specific requirements of that AS | Answer is YES |
| 2 | Should FFR2 be provided additional compensation as this product can be considered as ALSO providing CR (or a portion of it) | YES- Note if FFR2 is compensated for its contribution to CR, the recall of this FFR2 may be delayed. NO – ERCOT’s AS Methodology should be such that it takes into account the deployed FFR2 when determining the CR Target amounts in the AS Plan. NO – In case of SCED headroom shortage, there may be instances where all of the CR needs to be deployed. In this scenario, ERCOT would NOT want to use FFR2 as part of CR deployment to protect against Firm Load Shed due to G-2 (BAL-003) No – This will lead to the same MW being compensated for two AS Conditional NO – If the answer to 1 is YES, then as FFR2 AND CR2 has opportunity costs for energy and other AS incorporated into AS MCPCs, there is no need for this additional compensation – (double counting of opportunity costs may occur depending on how constraints are defined?) | Answer is NO |

The table below is an example of one way to setup the constraints for the procurement of AS. There are other ways to setup the required constraints for the procurement of AS. For example instead of a constraint to enforce a minimum amount of CR procurement from SCED dispatchable Resources (CR1), the constraint could be replaced with another constraint that enforces a maximum amount of CR procurement for non-SCED dispatchable Resources (CR2).

More discussion is required - both for the selection of constraints and the setup of the MCPCs for the different AS.

Note 1: As an illustration, the table below shows how the constraints need to be setup to have a limit on the maximum procurement of AS from demand side or a minimum amount of AS that needs to be procured from supply side:

- PFR and FFR constraints are setup so that

  - Ratio that equivalences 1 MW of FFR with R MW of PFR is incorporated

  - Limit on the maximum procurement from FFR1, FFR2

- CR and SR constraints are setup so that there is a minimum procurement target of CR and SR from Generation Resources

- FRRS-Up and FRRS-Dn constraints are setup so there is a limit on the maximum procurement of these AS

| ID | Constraints to procure AS | Equation | ShadowPrice | Comments |
| --- | --- | --- | --- | --- |
| 1 | Combined PFR + FFR procurement | PFR+R*(FFR1+FFR2) >= (PFR+FFR)TotalTarget (PFR+FFR)TotalTarget = Requirement (X+R*Y) minus (PFR+R*FFR) Self Arrangement | SPPFR+FFR | - Combined procurement allows opportunity cost of energy to be incorporated the resulting MCPCs. Also helps in mitigating liquidity concerns in FFR by combining the clearing with PFR offers - Constraint incorporates the Ratio that equivalences 1 MW of FFR with R MW of PFR - A QSE can self-arrange its PFR and FFR obligations separately or can substitute PFR for FFR using the applicable ratio R. - The maximum amount of FFR that can be self-arranged cannot exceed the Load Ratio Share multiplied by the minimum FFR requirement (Y). - In addition, the maximum amount of FFR1 that can be self-arranged cannot exceed the Load Ratio Share multiplied by the maximum FFR1 requirement (S) |
| 2 | Maximum FFR procurement | FFR1 + FFR2 <= FFRMAX-Target FFRMAX-Target = Max FFR (Z) minus FFR Self Arrangement | SPFFR-MAX | - Sets a maximum FFR (FFR1+FFR2) procurement target - This shadow price is less than or equal to zero - The maximum amount of FFR that can be self-arranged cannot exceed the Load Ratio Share multiplied by the minimum FFR requirement (Y). |
| 3 | Maximum FFR1 procurement | FFR1 <= FFR1MAX-Target FFR1MAX-Target =Max FFR1 (S) minus FFR1 Self Arrangement | SPFFR1-MAX | - Sets a maximum FFR1 procurement target - This shadow price is less than or equal to zero - In addition, the maximum amount of FFR1 that can be self-arranged cannot exceed the Load Ratio Share multiplied by the maximum FFR1 requirement (S) |
| 4 | CR procurement | CR1+CR2 >= CRTarget CRTarget = Requirement (T) minus (CR) Self Arrangement | SPCR | - A QSE can self-arrange its entire CR obligation using CR1. If the QSE decides to self-arrange a portion of its CR obligation using CR2, then the self-arrangement of CR2 cannot exceed the QSEs Load Ratio Share multiplied by the difference between CR Requirement and CR1 Min Requirement |
| 5 | Minimum CR1 procurement | CR1>= CR1Target CR1Target = Requirement (U) minus (CR1) Self Arrangement | SPCR1 | - Sets a minimum SCED dispatchable CR1 procurement target - Not a strong constraint (penalty cost for violating this constraint is relatively low) – or can use CR1 Demand curve to set the shadow price for this constraint. - The opportunity cost for energy is incorporated into this shadow price (SPCR1). If this constraint was redefined to be a maximum procurement target for CR2, then the previous constraint (ID# 4) would incorporate the opportunity costs for energy in its shadow price (SPCR) |
| 6 | SR procurement | SR1+SR2>= SRTarget SRTarget = Requirement (V) minus (SR) Self Arrangement | SPSR | - A QSE can self-arrange its entire SR obligation using SR1. If the QSE decides to self-arrange a portion of its SR obligation using SR2, then the self-arrangement of SR2 cannot exceed the QSEs Load Ratio Share multiplied by the difference between SR Requirement and SR1 Min Requirement |
| 7 | Minimum SR1 procurement | SR1>= SR1Target SR1Target = Requirement (W) minus (SR1) Self Arrangement | SPSR1 | - Sets a minimum SCED dispatchable SR1 procurement target - Not a strong constraint (penalty cost for violating this constraint is relatively low) – or can use SR1 Demand curve to set the shadow price for this constraint. - The opportunity cost for energy is incorporated into this shadow price (SPSR1). If this constraint was redefined to be a maximum procurement target for SR2, then the previous constraint (ID# 6) would incorporate the opportunity costs for energy in its shadow price (SPSR) |
| 8 | Regulation UP procurement | RegUp + FFRS-Up >= RegUpTarget RegUpTarget = Requirement (A) minus (RegUp + FRRS-Up) Self Arrangement | SPRegUp | - A QSE can self-arrange its entire RegUp obligation using RegUp. If the QSE decides to self-arrange a portion of its RegUp obligation using FRRS-Up, then the self-arrangement of FRRS-Up cannot exceed the QSEs Load Ratio Share multiplied by the FRRS-Up Max Requirement. |
| 9 | Maximum FRRS-Up procurement | FRRS-Up <= FRRS-UpMaxTarget FRRS-UpMaxTarget = Max FRRS-Up (B) minus (FRRS-Up) Self Arrangement | SPFRRSUp-MAX |  |
| 10 | Regulation DOWN procurement | RegDn + FRRS-Dn >= RegDnTarget RegDnTarget = Requirement (C) minus (RegDn + FRRS-Dn) Self Arrangement | SPRegDn | - A QSE can self-arrange its entire RegDn obligation using RegDn. If the QSE decides to self-arrange a portion of its RegDn obligation using FRRS-Dn, then the self-arrangement of FRRS-Dn cannot exceed the QSEs Load Ratio Share multiplied by the FRRS-Dn Max Requirement. |
| 11 | Maximum FRRS-Down procurement | FRRS-Dn <= FRRS-DnMaxTarget FRRS-DnMaxTarget = Max FRRS-Dn (D) minus (FRRS-Dn) Self Arrangement | SPFRRSDn-MAX |  |

| AS MCPC | Equation | Comments |
| --- | --- | --- |
| PFR | SPPFR+FFR |  |
| FFR1 | Minimum of R*SPPFR+FFR, or VOLL | Value of FFR is R multiplied by the value of PFR Note: The MCPC of FFR1 is capped at VOLL |
| FFR2 | Minimum of R*SPPFR+FFR, or VOLL | Value of FFR is R multiplied by the value of PFR Note: The MCPC of FFR2 is capped at VOLL |
| CR1 | SPCR+ SPCR1 |  |
| CR2 | SPCR+ SPCR1 | CR2 is valued the same as CR1 |
| SR1 | SPSR+ SPSR1 |  |
| SR2 | SPSR+ SPSR1 | SR2 is valued the same as SR1 |
| RegUp | SPRegUp |  |
| FRRS-Up | SPRegUp | FRRS-Up is valued the same as RegUp |
| RegDn | SPRegDn |  |
| FRRS-Dn | SPRegDn | FRRS-Down is valued the same as RegDn |

“Use of Frequency Response Metrics to Assess the Planning and Operating Requirements for Reliable Integration of Variable Renewable Generation” by Joseph H. Eto, Principal Investigator Lawrence Berkeley National Laboratory

Refer to ERCOT’s Discussion Paper “Future Ancillary Service in ERCOT” for further descriptions of the need for this service

http://www.ercot.com/content/meetings/ros/keydocs/2012/0614/08._LRs_Assessment_2012_ROS.ppt

“Use of Frequency Response Metrics to Assess the Planning and Operating Requirements for Reliable Integration of Variable Renewable Generation” by Joseph H. Eto, Principal Investigator Lawrence Berkeley National Laboratory