## Slide 1
ERCOT SOL Methodology for the Planning and Operations Horizons
Stephen Solis
2014 OTS

## Slide 2
Objectives
At the completion of this course of instruction you will:
Identify the purpose of the ERCOT SOL methodology.
Identify the related NERC Standards
Identify what is a System Operating Limit (SOL)
Identify what is an Interconnection Reliability Operating Limits (IROL)
Identify relationships and impacts between ERCOT and Transmission Planners/Transmission Operators

## Slide 3
Purpose of ERCOT SOL Methodology
Ensure System Operating Limits (SOLs) are determined based on an established methodology
Describes the methodology for determining Interconnection Reliability Operating Limits (IROLs)
Documents communications
Notes: To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies within the ERCOT Interconnection.
Describes the methodology for determining the subset of SOLs classified as Interconnection Reliability Operating Limits (IROLs), for the planning horizon and operations horizon within the ERCOT Interconnection
Documents the communications with other interested and affected entities.

## Slide 4: Why did it change?
Recommendations from Texas Reliability Entity in 2012
2011 Arizona/San Diego Blackout.
To increase clarity.
To improve on the criteria for determination of IROLs.
Combined the planning and operations horizon SOL methodologies for consistency and ensuring review of changes

## Slide 5: 2011 Arizona/San Diego Blackout
18 Failure to recognize Interconnection Reliability Operating Limits and Establish Valid System Operating Limits
24 Not Recognizing Relay Settings When Establishing SOLs
Notes: 18 Failure to recognize Interconnection Reliability Operating Limits and Establish Valid System Operating Limits
The cascading nature of the September 8th event indicates that an Interconnection Reliability Operating Limit (IROL) was violated, even though WECC did not recognize any in effect on that day, and that System Operating Limits (SOL) on Path 44 and Hassayampa-North Gila were not valid for the system on September 8, 2011
24 Not Recognizing Relay Settings When Establishing SOLs
An affected TO did not properly establish the SOL for two transformers, as the SOL did not recognize that the most limiting elements (protective relays) were set to trip below the established emergency rating. As a result, the transformers tripped prior to the facilities being loaded to their emergency ratings during the restoration process, which delayed the restoration of power to the Yuma load pocket.

## Slide 6: Related NERC Standards
System Operating Limits Methodology for the Planning Horizon : FAC-010-2.1
System Operating Limits Methodology for the Operations Horizon: FAC-011-2
Establish and Communicate System Operating Limits: FAC-014-2

## Slide 7: FAC-010-2.1
Applicable to Planning Authority only
R1 – R3 detail what the methodology must contain and address.
R4 details who the methodology must be distributed to.
R5 details the requirement to respond to comments within 45 calendar days (retired as part of “paragraph 81" efforts)

## Slide 8: FAC-011-2
Applicable to Reliability Coordinator only
Same requirements as FAC-010-2.1

## Slide 9: FAC-014-2
Applicable to RC, PA, TP, and TOP
R1 – R4: establish SOLs/IROLs consistent with the methodology
R5: Provide SOLS/IROLs to those with need
R6: PA communicate multiple contingencies resulting in stability limits to the RC.
Notes: R5. The Reliability Coordinator, Planning Authority and Transmission Planner shall each provide
its SOLs and IROLs to those entities that have a reliability-related need for those limits and
provide a written request that includes a schedule for delivery of those limits as follows:
  R5.1. The Reliability Coordinator shall provide its SOLs (including the subset of SOLs that
are IROLs) to adjacent Reliability Coordinators and Reliability Coordinators who
indicate a reliability-related need for those limits, and to the Transmission Operators,
Transmission Planners, Transmission Service Providers and Planning Authorities
within its Reliability Coordinator Area. For each IROL, the Reliability Coordinator
shall provide the following supporting information:
    R5.1.1. Identification and status of the associated Facility (or group of Facilities)
that is (are) critical to the derivation of the IROL.
    R5.1.2. The value of the IROL and its associated Tv.
    R5.1.3. The associated Contingency(ies).
    R5.1.4. The type of limitation represented by the IROL (e.g., voltage collapse,
angular stability).
  R5.2. The Transmission Operator shall provide any SOLs it developed to its Reliability
Coordinator and to the Transmission Service Providers that share its portion of the
Reliability Coordinator Area.
  R5.3. The Planning Authority shall provide its SOLs (including the subset of SOLs that are
IROLs) to adjacent Planning Authorities, and to Transmission Planners, Transmission
Service Providers, Transmission Operators and Reliability Coordinators that work
within its Planning Authority Area.
  R5.4. The Transmission Planner shall provide its SOLs (including the subset of SOLs that
are IROLs) to its Planning Authority, Reliability Coordinators, Transmission
Operators, and Transmission Service Providers that work within its Transmission
Planning Area and to adjacent Transmission Planners.

## Slide 10: What is a SOL?
The value (such as MW, MVar, Amperes, Frequency or Volts) that satisfies the most limiting of the prescribed operating criteria for a specified system configuration to ensure operation within acceptable reliability criteria. System Operating Limits are based upon certain operating criteria. These include, but are not limited to:
  • Facility Ratings (Applicable pre- and post-Contingency
  equipment or facility ratings)
  • Transient Stability Ratings (Applicable pre- and post-
  Contingency Stability Limits)
  • Voltage Stability Ratings (Applicable pre- and post-
  Contingency Voltage Stability)
  • System Voltage Limits (Applicable pre- and post-
  Contingency Voltage Limits)
Notes: The value (such as MW, MVar, Amperes, Frequency or Volts) that satisfies the most limiting of the prescribed operating criteria for a specified system configuration to ensure operation within acceptable reliability criteria. System Operating Limits are based upon certain operating criteria. These include, but are not limited to:
  • Facility Ratings (Applicable pre- and post-Contingency
  equipment or facility ratings)
  • Transient Stability Ratings (Applicable pre- and post-
  Contingency Stability Limits)
  • Voltage Stability Ratings (Applicable pre- and post-
  Contingency Voltage Stability)
  • System Voltage Limits (Applicable pre- and post-
  Contingency Voltage Limits)
There are several limits that exist on the system from facility ratings to stability limits that ensure operation within acceptable reliability criteria.
Typically, the most restrictive limits are the facility ratings which make up the majority of the System Operating Limits.
Additionally stability limits or interface limits may be the most restrictive and thus constitute additional System Operating Limits.

## Slide 11: What is a SOL?
Several limits ensure operation within acceptable reliability criteria
  Facility ratings are the majority of the SOLs.
    Typically, the most restrictive
  Stability limits or Interface limits constitute additional SOLs
    may be the most restrictive

## Slide 12: What is a SOL?
Example 1:
  Line A to B 138kV has a thermal facility rating of 100 MVA continuous rating.
  Line A to B 138kV has a voltage stability limit of 150 MVA
  Line A to B 138kV has a dynamic stability limit of 130 MVA
What is its System Operating Limit?
  Answer: Line A to B 138kV has a thermal facility rating of 100 MVA continuous rating which is the most restrictive of the limits and is thus the System Operating Limit.

## Slide 13: What is a SOL?
Example 2:
  Line A to B 138kV has a thermal facility rating of 100 MVA continuous rating.
  Line A to B 138kV has a voltage stability limit of 90 MVA
  Line A to B 138kV has a dynamic stability limit of 130 MVA
What is its System Operating Limit?
  Answer: Line A to B has a voltage stability limit of 90 MVA which is the most restrictive of the limits and is thus the System Operating Limit.

## Slide 14: What is a SOL?
Example 3:
  Line A to B 138kV has a thermal facility rating of 100 MVA Normal (Continuous) rating.
  Line A to B 138kV has a thermal facility rating of 120 MVA Emergency (2 hour) rating.
  Line A to B 138kV has a thermal facility rating of 140 MVA 15 minute (Load Shed) rating.
What is its System Operating Limit?
  Answer: All of the above. Each facility rating is a System Operating Limit with an associated time frame. The facility can be operated at 100 MVA continuously, up to 120 MVA for up to 2 hours, and up to 140 MVA for up to 15 minutes.

## Slide 15: Steady State Voltage SOLs
Steady State Voltage SOLs in ERCOT:
  (1) 0.95 per unit to 1.05 per unit in the pre-contingency state (and with all facilities in service in the planning horizon)
  (2) 0.90 per unit to 1.10 per unit in the post-contingency state (following a NERC Category B or C contingency (where appropriate)
These are default unless otherwise communicated by the Facility Owner.

## Slide 16: Additional SOLs
Result from studies indicating a more restrictive limit that results in the following:
  Transient, dynamic instability
    (loss of a generator due to the instability)
  Voltage instability
    (uncontrolled voltage loss)
  Cascading or uncontrolled separation;
  Post disturbance frequency
    outside the range 59.4 Hz to 60.4 Hz

## Slide 17: Additional SOLs (continued)
    Manual system adjustments,
      e.g., system reconfiguration between contingencies in an N-1-1 Category C event, or load shedding are needed in order to prevent Cascading or transient, dynamic, or voltage instability.

## Slide 18: Additional SOLs (continued)
Voltage stability margin in the planning horizon is not sufficient to maintain post-transient voltage stability under the following two conditions for an ERCOT or TP-defined area:
  A 5% increase in Load above expected peak supplied from resources external to the ERCOT or TP-defined area and NERC Category A or B operating conditions; or
  A 2.5% increase in Load above expected peak supplied from resources external to the ERCOT or TP-defined area and NERC Category C operating conditions;

## Slide 19: Sub Bulk Electric System(BES) facilities
In ERCOT, 69kV facilities are considered transmission and are monitored and secured.
The SOL methodology applies to BES facilities.
Non-BES facilities and contingencies can be evaluated for their effect in determining a SOL on BES facilities.
Non-BES facilities have limits that are enforced, just not SOLs as defined by NERC.

## Slide 20: When is a SOL and IROL?
Interconnection Reliability Operating Limit (IROL)
  SOL that, if violated, could lead to:
    instability,
    uncontrolled separation, or
    Cascading Outages
  Cascading
    Uncontrolled successive loss of system elements
      widespread electric service interruption that cannot be restrained from sequentially spreading beyond an area predetermined by studies.

## Slide 21: When is a SOL an IROL?
An SOL is an IROL if:
      Loss of load (manual or auto) is greater than 6% of the ERCOT Interconnection load level used in the study
  Triggers automatic under-frequency load shedding
  Observable inter-area oscillation with damping ratio less than 3%.
Notes:       Loss of load in the Cascading or voltage collapse, either through manual action or as a consequence of the event (including loss of load as a result of Under Voltage Load Shedding (UVLS), is greater than 6% of the ERCOT Interconnection load level used in the study
  Trigger of automatic under frequency load shedding
  Observable inter-area oscillation with damping ratio less than 3%.

## Slide 22: Where did the 6% come from?
Previous SOL methodologies used a 20% load threshold and exercised engineering judgment when the loss of load in a study was less than 20%.
6% is a conservative value so that a loss of load should not cause generation to begin tripping off as a result of the loss of load (over-frequency).
  ERCOT Operating Guides Section 2.6.2 requires no automatic tripping below 60.6 Hz.
  Any set points between 60.6Hz and 61.6Hz should not trip within 9 minutes.

## Slide 23: Load Loss in Study
20%
Load Loss in Study
6%
Previous Versions
Current Version
Load Loss in Study
Engineering
Judgment
IROL
IROL
Defend why a SOL with a consequence of load loss greater than 6% is not an IROL
Defend why a SOL with less than 20% load loss should be an IROL.

## Slide 24: ERCOT ISO and Transmission Planners/Transmission Operators
ERCOT ISO:
  single RC and PA for the ERCOT Interconnection.
  distributes this methodology to all TPs and TOPs in the ERCOT Interconnection.
  establishes SOLs in accordance with the SOL methodology.
  responds to comments on the SOL methodology.
  provides SOLs (including IROLs) to TOPs and TPs in the ERCOT Interconnection that provide a written request that includes a schedule for delivery of those limits.

## Slide 25: ERCOT ISO and Transmission Planners/Transmission Operators
TPs and TOPs
  establish SOLs in accordance with the SOL methodology.
  provide any SOLs to ERCOT ISO.
    Facility Ratings
    Special Transfer Limits
    Stability Limits
  should incorporate any SOLs that are provided to them by ERCOT ISO or adjacent entities that affect their area into their studies for determining SOLs.
TPs provide SOLs to adjacent TPs and TOPs

## Slide 26
Summary
The SOL Methodology ensures that SOLs used in the reliable operation of the ERCOT System are determined based on an established methodology.
The SOL is the most restrictive of all ratings or limits on a BES facility or element.
IROLs are the subset of SOLs that meet the IROL criteria.
SOLs are distributed amongst TPs, TOPs, and ERCOT ISO.

## Slide 27
References
1.) NERC Glossary of Terms
http://www.nerc.com/pa/Stand/Glossary%20of%20Terms/Glossary_of_Terms.pdf
2.) NERC Reliability Standards
http://www.nerc.com/pa/Stand/Reliability%20Standards%20Complete%20Set/RSCompleteSet.pdf
3.) ERCOT Operating Guides
http://www.ercot.com/content/mktrules/guides/noperating/2013/1007/October_7,_2013_Nodal_Operating_Guides.pdf
4.) Arizona-Southern California Outages on September 8, 2011
http://www.ferc.gov/legal/staff-reports/04-27-2012-ferc-nerc-report.pdf
5.) ERCOT System Operating Limit Methodology for the Planning and Operations Horizon
http://planning.ercot.com/login/login (Home > Procedures > Planning Horizon Limits Documents. )

## Slide 28
Questions
?
?

## Slide 29
1. The purpose of the ERCOT SOL methodology is to ensure System Operating Limits (SOLs) is determined based on a ______________ ______________?
established methodology
load forecast
network model
increased clarity

## Slide 30
Which of the following NERC related standards are applicable to System Operating Limits (SOLs)?
FAC-010-2.1
FAC-011-2
FAC-014-2
All of the above

## Slide 31
____________ ratings are the majority of the System Operating Limits (SOLs) and are typically the ________ restrictive.
Facility; most
Generator; most
Wave trap; least
Insulator; most

## Slide 32
An SOL is an IROL if loss of load (manual or automatic) is greater than _________ of the ERCOT interconnection load level used in the study.
4%
3%
5%
6%

## Slide 33
ERCOT ISO ___________ SOLs in accordance with the SOL methodology.
establishes
collects
protects
auctions