| PGRR Number | 028 | PGRR Title | Evaluation of Compliance with Reactive Requirements |
| --- | --- | --- | --- |

| Date | September 23, 2013 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Paul Tan |
| E-mail Address | ptan@ercot.com |
| Company | ERCOT |
| Phone Number | (512) 248-4181 |
| Cell Number |  |
| Market Segment | Not applicable. |

Comments

Electric Reliability Council of Texas, Inc. (ERCOT) submits these comments to address concerns on varying voltage conditions across the ERCOT System.  ERCOT and the interconnecting Transmission Service Provider (TSP) will designate a range of voltages for the Generation Resource and utilize the Reactive Power study provided by the Interconnecting Entity to verify compliance with the Reactive Power requirements.

Revised Proposed Guide Language

5.6.1	Evaluation of Compliance with Reactive Power Requirements

(1)	Following ERCOT’s receipt of a new or amended Standard Generation Interconnection Agreement (SGIA), ERCOT will evaluate whether a proposed All-Inclusive Generation Resource is designed to comply with Reactive Power capability and voltage control requirements as specified by Protocol Section 3.15, Voltage Support, this Planning Guide, Nodal Operating Guides, and Other Binding Documents.

(2)	ERCOT and the interconnecting Transmission Service Provider (TSP) shall review the engineering study that is required of a Generation Resource under paragraph (3)(d) of Protocol Section 3.15 in order to determine if the Generation Resource meets the Reactive Power capability requirements at the Point of Interconnection (POI).

(3)	ERCOT and the interconnecting TSP shall establish expected Voltage Profiles and operating ranges for the Generation Resource.

(a)	ERCOT and the interconnecting TSP shall confirm that the Generation Resource is able to provide Reactive Power without adjustment to no-Load transformer taps or without Off-Line adjustments for the operating range at the initial Voltage Profile.

(b)	ERCOT and the interconnecting TSP shall confirm that the Generation Resource is able to provide Reactive Power, with adjustments to no-Load transformer taps or Off-Line adjustments if necessary, for the operating range at subsequent expected Voltage Profiles.

(4)	ERCOT shall indicate in its review whether the design of the proposed Generation Resource complies with the Reactive Power capability requirements established in Protocol Section 3.15, this Planning Guide, Nodal Operating Guides, and Other Binding Documents.  Nothing in this Section 5.6.1 shall be construed to change the Reactive Power and voltage control requirements prescribed in the Protocols.