| NOGRR Number | 129 | NOGRR Title | Implement Operational Preparedness for Geomagnetic Disturbances |
| --- | --- | --- | --- |

| Date | April 22, 2014 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Dan Woodfin |
| E-mail Address | dan.woodfin@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-3115 |
| Cell Number | 512-750-0655 |
| Market Segment | Not applicable. |

Comments

ERCOT has discussed the 4/16/14 Austin Energy comments with AE and offers revised language below.

Revised Cover Page Language

| Nodal Operating Guide Sections Requiring Revision | 1.4, Definitions 4.7, Geomagnetic Disturbance Operating Plan (new) 4.7.1, Monitoring and Dissemination of Space Weather Information (new) 4.7.2 Development and Submission of TO GMD Operating Procedures or Processes (new) 4.7.3 ERCOT’s GMD Operating Plan and Review of TO GMD Operating Procedures or Processes (new) |
| --- | --- |
| Revision Description | This Nodal Operating Guide Revision Request (NOGRR) sets up an ERCOT Region coordination process through which ERCOT and Transmission Operators (TOs) will develop Geomagnetic Disturbance (GMD) operating documents and communicates such information. |

Revised Proposed Guide Language

1.4	Definitions

Geomagnetic Disturbance (GMD)

A disturbance of the earth’s magnetic field caused by the interaction of that field with the effects of solar storms.  These GMDs may result in induced currents that may negatively affect power system equipment.

4.7       Geomagnetic Disturbance Operating Plan

4.7.1	Monitoring and Dissemination of Space Weather Information

(1)	ERCOT shall maintain procedures to receive Geomagnetic Disturbance (GMD) alerts and warnings issued by the National Oceanic and Atmospheric Administration (NOAA).

(2)	ERCOT shall implement and maintain procedures to provide GMD alerts and warnings to Transmission Operators (TOs).

(3)	Other forecasted and current space weather information is publicly available directly through the NOAA website.

4.7.2	Development and Submission of TO GMD Operating Procedures or Processes

(1)	Each TO that operates transmission equipment that includes a power transformer with a high side wye-grounded winding with terminal voltage greater than 200kV shall develop a GMD operating  procedure or process to mitigate the effects of GMD events on the reliable operation of its system.

(2)	Each TO GMD operating procedure or process shall be provided to ERCOT within three months following approval by the Federal Energy Regulatory Commission (FERC) of North American Electric Reliability Corporation (NERC) Standard EOP-010-1, Geomagnetic Disturbance Operations.  Updates to the plan shall be provided to ERCOT by March 15 of each subsequent year.

(3)	Each TO GMD operating procedure or process shall include:

(a)	A procedure to receive GMD alerts and warnings from ERCOT;

(b)	A description of operational actions the TO intends to take to mitigate the effects of a GMD event.  This description shall include:

(i)	The triggering event for each action;

(ii)	A detailed explanation of each operational action;

(iii)	A list of Entities with which the TO must coordinate, if any, including any actions requested of other Entities in the ERCOT Region mn order to implement the TOSs GMD oOerating procedure or process; Pnd

(iv)	The conditions under which each action would be terminated.

(c)	A procedure for reporting to ERCOT any unusual operational information that could be the result of GMD, such as high reactive loading, Mega Volt-Amperes reactive (MVAr) or voltage swings, high geomagnetically induced current on monitored transformers or equipment malfunctions.

    - ERCOT’s GMD Operating Plan and ERCOT Review of TO GMD Operating Procedures or Processes

(1)	ERCOT shall develop a GMD operating plan and post it on the Market Information System (MIS) Public Area.

(2)	The ERCOT GMD operating plan shall coordinate the TO GMD operating procedures or processes. This coordination is intended to ensure the TO GMD operating procedures or processes are not in conflict with one another and is not intended to be a review of the technical aspects of the TOSGMD oOerating procedures or processes.P

(3)	In preparing the ERCOT GMD operating plan, ERCOT shall identify and notify the relevant TOs of any conflicts between the different TO GMD operating procedures or processes and any unacceptable actions requested of ERCOT in the TO operating procedures or processes.

(a)	ERCOT and the TOs shall coordinate development of any required modifications to the TO GMD operating procedures or processes necessary to resolve these conflicts or unacceptable actions.

(b)	A TO shall make the resulting modifications to its GMD operating procedures or processes.

(4) The ERCOT GMD operating plan shall include:

(a) A description of activities designed to mitigate the effects of GMD events on the reliable operation of the interconnected transmission system; and

(b) Any operating actions required of ERCOT by the TO GMD operating procedures or processes and approved by ERCOT for inclusion in the ERCOT GMD operating plan.