## Slide 1: PDCWG Report to ROS
Sydney Niemeyer Chair
NRG Energy
Don Blackburn Vice Chair
Luminant Energy

## Slide 2: May 28 Meeting
Manual Deployment and Recall of Responsive Reserve Service during Scarcity Conditions.
  Discussion Items:
    Loss of available Primary Frequency Response.
    Concern with ERCOT’s ability to estimate available Primary Frequency Response.
    Resource Real-time HSL accuracy.
    ERCOT logic change needed for manual Recall to avoid auto recall based on frequency returning to 59.970 Hz.
    ERCOT researched and found only 3 times the manual deployment would have been executed since April 2012.

## Slide 3: Loss of Primary Frequency Response
As RRS is manually deployed and SCED utilizes the capacity, Primary Frequency Response and the depth of that response will be depleted.
  Higher risk of not meeting BAL-003-1
  Loss of Load risk increases significantly.
  Fewer Resources will be maintaining frequency stability increasing Resource output movement and resulting loss of controllability.
  If RRS capacity is not manually deployed, frequency will decay and the energy will be delivered through Primary Frequency Response anyway.

## Slide 4: Estimating Available Primary Frequency Response in Real Time
The available Primary Frequency Response can change quickly depending on loading of Resources.
Accurate HSL’s and identification of how much spinning reserve is actually frequency responsive is greatest concern in estimation.
Deploys RRS before Regulation Up Service since REGUP is deployed based on grid frequency.

## Slide 5: Resource HSL Accuracy
Augmented capacity on Resources that is contained within the HSL is typically not frequency responsive. Telemetry of this information is not available at this time.
Ambient temperature and humidity impacts HSLs. Most Resources do not update HSL in Real Time based on current conditions.
  While reviewing Disturbance Reports, it is apparent that there is greater than a 2% error in their HSL on many Resources.
  ERCOT discounts HSLs in the PRC calculation by:
    Decrease HSL by 1% if ambient temp </= 95 degrees F.
    Decrease HSL by 2% if ambient temp > 95 degrees F.

## Slide 6: RRS Recall Logic
Presently RRS is automatically recalled when frequency recovers to 59.970 Hz following a deployment at 59.910 Hz.
ERCOT will have a logic change implemented prior to July 1 for the manual deployment of RRS. This will allow RRS to remain deployed independent of grid frequency when deployed manually.

## Slide 7: Frequency of Manual Deployment of RRS
ERCOT researched historical PRC data.
  Since April 2012 there would have been 3 manual deployments of RRS based on the criteria in this procedure.

## Slide 8: Other Meeting Subject Discussions
Resource GREDP review for the month of May through the 26th.
  Status quo on number of Resources struggling to meet the metric.
  Significantly poor performers have been contacted by ERCOT. Escalation to TRE may be necessary on a few.
BAL-001-TRE-1 implementation timeline was reviewed. ERCOT project internally to start in late June to meet BA requirements.
  TRE expressed concern that FAST is suggesting an increase if governor dead-bands on some Resources and the resulting decrease in Primary Frequency Response from these Resources.

## Slide 9: Other Meeting Subject Discussions
TRE Update:
  NERC Standard activity
    PRC-005 adding “sudden pressure relay” to the list of covered protective relays.
    PRC-002 Disturbance Monitoring adding phasor monitoring to Resources for model verification.
    Bulk Electric System definition webinar June 5th.
    NERC State of Reliability Report identified significant improvement in 2013 in Primary Frequency Response performance in ERCOT.
    Significant drop in poor performing Resources in ERCOT Disturbance Analysis reports during 2013.
ERCOT LFC Tuning Changes implemented.
  May 27 at 09:30 ERCOT made LFC tuning changes.
  Immediate improvement in CPS1 of 8 to 10 points observed since the change. CPS2 improvement as well as Time Control is better.

## Slide 10: ERCOT Disturbance Reports Reviewed
May 1, 2014 Frequency Event.
  15 Resources had issues with Primary Frequency Response.
    8 of these Resources may have augmented spinning reserve and therefore not frequency responsive.
    3 Resources had possible HSL errors.
May 13, 2014 High Frequency Event- DC tie trip.
  Present evaluation tool does not accurately measure response to High frequency deviations.
  Wind Generators as a fleet performed well.
May 15, 2014 Frequency Event
  4 Resources had issues with Primary Frequency Response.
    One Resource had early PFR withdrawal.
    Three Resources had low PFR delivery with one of these believed to have augmented spinning reserve capacity.
    One Resource did not follow SCED deployments during the frequency recovery period.

## Slide 11: ERCOT Frequency Control Report May 2014
Sydney Niemeyer NRG Energy
June 3, 2014

## Slide 12: Notes
Time error values from NRG True Time device can be slightly different from ERCOT’s Time Error but the daily delta times should be accurate.
CPS 1 and CPS 2 data for May is from NRG Frequency True Time device and will be slightly different from ERCOT’s measure. The monthly CPS1 score is typically within +/-0.05.

## Slide 13: Ercot frequency control
BAL-001 CPS 1 & 2 Performance, RMS 1 and Frequency Profile

## Slide 14
ERCOT LFC Tuning Change @ 09:30

## Slide 16
CPS1 12 Month Rolling Average = 162.60

## Slide 21
60.010 <= HZ < 60.015

## Slide 23: ERCOT Time error and time correction
Time Error History

## Slide 24: Time Error Corrections
Eleven slow Time Error Corrections were executed in May.
Other than the days with the TECs, no days had positive time error.

## Slide 27
Time Correction History

## Slide 30: Ercot primary frequency response performance
BAL-003-1 Interconnection Frequency Response and Bias Measure.

## Slide 31
ERCOT Primary Frequency Response – BAL-003-1
2015 Bias and Frequency Response Measure

## Slide 32: Ercot total energy and wind production
October Total ERCOT Energy and Total Energy Production from Wind Resources.