| NOGRR Number | 129 | NOGRR Title | Implement Operational Preparedness for Geomagnetic Disturbances |
| --- | --- | --- | --- |
| Date Posted |  | March 12, 2014 |  |
| Requested Resolution |  | Normal |  |
| Nodal Operating Guide Sections Requiring Revision |  | 1.4, Definitions 4.7, Geomagnetic Disturbance Operating Plans (new) 4.7.1, Monitoring and Dissemination of Space Weather (new) 4.7.2 Development and Submission of TSP GMD Operating Plans (new) 4.7.3 ERCOT Review of GMD Operating Plans (new) |  |
| Other Binding Documents Requiring Revision or Related Revision Requests |  | None. |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) sets up a process through which ERCOT and Transmission Service Providers (TSPs) will develop Geomagnetic Disturbance (GMD) Operating Plans that will be coordinated across the ERCOT Region and provides for communication of information regarding those Plans. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |

| Business Case |  |
| --- | --- |
| Qualitative Benefits | Allows ERCOT and TSPs to meet requirements of North American Electric Reliability Corporation (NERC) Standard EOP-010, Geomagnetic Disturbance Operations, which is pending Federal Electric Reliability Commission (FERC) approval. |
| Quantitative Benefits |  |
| Impact to Market Segments |  |
| Credit Implications |  |
| Other |  |

| Sponsor |  |
| --- | --- |
| Name | Paul Rocha on behalf of Geomagnetic Disturbance Task Force (GMDTF) |
| E-mail Address | Paul.rocha@centerpointenergy.com |
| Company | CenterPoint Energy |
| Phone Number | 713-207-2768 |
| Cell Number |  |
| Market Segment | Investor Owned Utility (IOU) |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Lisa Trow |
| E-Mail Address | ltrow@ercot.com |
| Phone Number | 512-248-6521 |

Proposed Guide Language Revision

1.4	Definitions

Geomagnetic Disturbance (GMD)

A disturbance of the earth’s magnetic field caused by the interaction of that field with the effects of solar storms.  These GMDs may result in induced currents that may negatively affect power system equipment.

4.7       Geomagnetic Disturbance Operating Plan

4.7.1	Monitoring and Dissemination of Space Weather

(1)	ERCOT shall maintain procedures to receive Geomagnetic Disturbance (GMD) alerts and warnings issued by the National Oceanic and Atmospheric Administration (NOAA).

(2)	ERCOT shall maintain procedures to provide GMD alerts and warnings to Transmission Service Providers (TSPs).

4.7.2	Development and Submission of TSP GMD Operating Plans

(1)	Each TSP that operates Transmission equipment with a voltage of 200kV or higher shall develop a GMD Operating Plan

(2)	Each TSP GMD Operating Plan shall be provided to ERCOT within three months following approval by the Federal Energy Regulatory Commission (FERC) of North American Electric Reliability Corporation (NERC) Standard EOP-010-1, Geomagnetic Disturbance Operations.  Updates to the plan shall be provided to ERCOT by March 15 of each subsequent year.

(3)	The GMD Operating Plan shall include:

(a)	A procedure to receive GMD alerts and warnings from ERCOT;

(b)	A description of operational actions the TSP plans to take to mitigate the effects of a GMD event.  This description shall include:

(i)	The triggering event for each action;

(ii)	A detailed explanation of each operational action;

(iii)	A list of any Entities with which the TSP must coordinate and any actions other Entities in the ERCOT Region, including ERCOT, must take in order to implement the TSP’s GMD Operating Plan; and

(iv)	The conditions under which each action would be terminated.

(c)	A procedure for reporting to ERCOT any unusual operational information that could be the result of GMD, such as high reactive loading, Mega Volt-Amperes reactive (MVAr) or voltage swings, high geomagnetically induced current on monitored transformers or equipment malfunctions.

    - ERCOT Review of GMD Operating Plans

(1)	ERCOT shall post its GMD Operating Plan on the Market Information System (MIS) Public Area.

(2)	The ERCOT GMD Operating Plan shall coordinate the TSP GMD Operating Plans.  This coordination is intended to ensure the TSP GMD Operating Plans are not in conflict with one another and is not intended to be a review of the technical aspects of the TSP GMD Operating Plans.

(3)	The ERCOT GMD Operating Plan should include any operating actions required of ERCOT by the TSP GMD Operating Plans and approved by ERCOT for inclusion in the ERCOT GMD Operating Plan.

(4)	In preparing the ERCOT GMD Operating Plan, ERCOT should identify and notify the relevant TSPs of any conflicts between the different TSP GMD Operating Plans and any unacceptable operating actions required of ERCOT in a TSP GMD Operating Plan.

(a)	ERCOT and the TSPs will coordinate development of any required modifications to the TSP GMD Operating Plans necessary to resolve these conflicts or unacceptable actions.

(b)	A TSP shall make the resulting modifications to its GMD Operating Plan.