| PGRR Number | 028 | PGRR Title | Evaluation of Compliance with Reactive Requirements |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Tabled |
| Date of Decision |  | November 14, 2013 |  |  |
| Proposed Effective Date |  | To be determined. |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Planning Guide Section Requiring Revision |  | 5.6.1, Evaluation of Compliance with Reactive Power Requirements (new) |  |  |
| Protocol Section(s) Requiring Revision |  | None. |  |  |
| Revision Description |  | This Planning Guide Revision Request (PGRR) defines ERCOT’s process for evaluating proposed Generation Resources’ abilities to provide Reactive Power. Protocol Section 3.15, Voltage Support, defines reactive capability requirements for Generation Resources. Paragraph (3) of Protocol Section 16.5, Registration of a Resource Entity, requires ERCOT to opine upon the capability of the proposed Generation Resource’s ability to meet these requirements. |  |  |
| Reason for Revision |  | This PGRR is in response to concerns raised during the October 15, 2012 Photovoltaic and Storage Workshop; and clarifies how Entities proposing Generation Resources must design their new facilities. |  |  |
| Procedural History |  | - On 2/12/13, PGRR028 and an Impact Analysis were posted. - On 2/27/13, the Planning Working Group (PLWG) considered PGRR028. - On 3/26/13, Oncor comments were posted. - On 3/27/13, the PLWG again considered PGRR028. - On 9/23/13, ERCOT comments were posted. - On 9/25/13, the PLWG again considered PGRR028. - On 10/14/13, CenterPoint Energy comments were posted. - On 10/23/13, the PLWG considered the 9/25/13 PLWG Report and Impact Analysis for PGRR028. - On 11/14/13, ROS considered PGRR028. |  |  |
| PLWG Decision |  | On 2/27/13, the PLWG was in consensus to table PGRR028 for one month. On 3/27/13, the PLWG was in consensus to table PGRR028. On 9/13/13, the PLWG was in consensus to recommend approval of PGRR028 as amended by the 9/23/13 ERCOT comments and as revised by the PLWG. On 10/23/13, the PLWG was in consensus to endorse and forward the 9/25/13 PLWG Report as amended by the 10/14/13 CenterPoint Energy comments and the Impact Analysis for PGRR028 to ROS. |  |  |
| Summary of PLWG Discussion |  | On 2/27/13, participants requested that PGRR028 be tabled to allow additional time for review. On 3/27/13, the feasibility of proposed Generation Resources to comply with existing Reactive Power requirements was discussed. It was requested that ERCOT develop comments to define appropriate performance parameters to be used when evaluating a proposed Generation Resource’s Reactive Power. On 9/13/13, the 9/23/13 ERCOT comments were reviewed. On 10/23/13, the 10/14/13 CenterPoint Energy comments were reviewed. |  |  |
| ROS Decision |  | On 11/14/13, ROS unanimously voted to table PGRR028 and refer the issue to PLWG. All Market Segments were present for the vote. |  |  |
| Summary of ROS Discussion |  | On 11/14/13, there was discussion regarding the expectation for Generation Resources to provide an operating range at anticipated future Voltage Profiles and the criteria used to determine that future date. There was agreement that the language needed clarification to accurately reflect the intent. |  |  |

| Business Case |  |  |
| --- | --- | --- |
| Business Case | 1 | - Clarifies ERCOT’s process of evaluating proposed Generation Resources. |

| Sponsor |  |
| --- | --- |
| Name | John Adams |
| E-mail Address | jadams@ercot.com |
| Company | ERCOT |
| Phone Number | (512) 248-3130 |
| Cell Number |  |
| Market Segment | Not applicable. |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Sandra Tindall |
| E-Mail Address | stindall@ercot.com |
| Phone Number | (512) 248-3867 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| Oncor 032613 | Revised the voltage range Generation Resources should comply with in order to accommodate varying voltage conditions across the ERCOT System. |
| ERCOT 092313 | Addressed concerns on the varying voltage conditions across the ERCOT System. |
| CenterPoint Energy 101413 | Proposed revisions to state that ERCOT has the ultimate responsibility for determining Generation Resource compliance with Reactive Power requirements. |

Proposed Guide Language Revision

5.6.1	Evaluation of Compliance with Reactive Power Requirements

(1)	Following ERCOT’s receipt of a new or amended Standard Generation Interconnection Agreement (SGIA), ERCOT will evaluate whether a proposed All-Inclusive Generation Resource is designed to comply with Reactive Power capability and voltage control requirements as specified by Protocol Section 3.15, Voltage Support, this Planning Guide, Nodal Operating Guides, and Other Binding Documents.

(2)	ERCOT in consultation with the interconnecting Transmission Service Provider (TSP) shall review the engineering study or performance testing that is required of a Generation Resource under paragraph (3)(d) of Protocol Section 3.15 in order to determine if the Generation Resource meets the Reactive Power capability requirements at the Point of Interconnection (POI).

(3)	ERCOT in cooperation with the interconnecting TSP shall establish anticipated Voltage Profiles and operating ranges for the Generation Resource.

(a)	ERCOT in consultation with the interconnecting TSP shall confirm that the Generation Resource is able to provide Reactive Power without adjustment to no-Load transformer taps or without Off-Line adjustments for the operating range at the anticipated initial Voltage Profile.

(b)	ERCOT in consultation with the interconnecting TSP shall confirm that the Generation Resource is able to provide Reactive Power, with adjustments to no-Load transformer taps or Off-Line adjustments if necessary, for the operating range at anticipated future Voltage Profiles.

(4)	ERCOT shall indicate in its review whether the design of the proposed Generation Resource complies with the Reactive Power capability requirements established in Protocol Section 3.15, this Planning Guide, Nodal Operating Guides, and Other Binding Documents.  Nothing in this Section 5.6.1 shall be construed to change the Reactive Power and voltage control requirements prescribed in the Protocols.