March 2014 ERCOT Monthly Operations Report

Reliability and Operations Subcommittee Meeting

May 8, 2014

Table of Contents

1.	Report Highlights	1

2.	Frequency Control	2

2.1.	Frequency Events	2

2.2.	Responsive Reserve Events	3

2.3.	Load Resource Events	3

2.4.	PMU Events	3

3.	Reliability Unit Commitment	3

4.	Wind Generation as a Percent of Load	5

5.	Congestion Analysis	5

5.1.	Notable Constraints for March	5

5.2.	Generic Transmission Limit Congestion	7

5.3.	Congestion Costs for Calendar Year 2014	7

6.	System Events	8

6.1.	ERCOT Peak Load	8

6.2.	Load Shed Events	8

6.3.	Stability Events	8

6.4.	TRE/DOE Reportable Events	8

6.5.	New/Updated RAPs and PCAPs	8

6.6.	New/Modified/Removed SPS	8

6.7.	New Procedures/Forms/Operating Bulletins	9

7.	Emergency Conditions	9

7.1.	OCNs	9

7.2.	Advisories	9

7.3.	Watches	9

7.4.	Emergency Notices	9

8.	Application Performance	9

8.1.	TSAT/VSAT Performance Issues	9

8.2.	Communication Issues	9

9.	Net-Forecast Bias Applied to NSRS Procurement for April 2014	10

10.	Appendix A: Real-Time Constraints	11

# Report Highlights

The freezing temperatures of January and February gave way to milder weather in March after a final cold snap at the beginning of the month. As a result, there was less activity on the ERCOT Interconnection than in recent months. Operations continued to note fewer frequency events and RRS deployments than what had been observed during the winter. The amount of SCED congestion did increase slightly in March. However, this was primarily due to ongoing outages. ERCOT also reached a new wind generation record of 10,296 MW on March 26. This accounted for 29 percent of the load at the time and surpassed the previous record by over 600 MW. In addition, a separate wind penetration record of 38.43% was reached on March 27.

Highlights of this report:

- The unofficial ERCOT peak for March was 54,549 MW.

- The ERCOT region reached a new wind generation record of 10,296 MW on March 26.

- ERCOT also reached a new wind penetration record on March 27, where 9,868 MW served 38.43% of the load.

- There were five frequency events in March, two of which were significant enough for PMU data to be captured. The ERCOT system transitioned well in each case.

- There were five instances where Responsive Reserves were deployed. All of these were the result of frequency events. There were no Load Resource deployments in March.

- RUC Commitments continued in March, primarily due to voltage stability in the Rio Grande Valley during ongoing outages in the area.

- There was a slight increase in the amount of SCED congestion in March, mainly due to ongoing outages.

- ERCOT did not experience any significant system events in March.

- ERCOT Applications performed well. There were no issues in March.

# Frequency Control

## Frequency Events

The ERCOT Interconnection experienced five frequency events in March, all of which resulted from Resource trips. The average event duration was approximately 55 seconds, which was consistent with the system performance observed in previous months. Further details on the Resource trip events can be seen in the Performance Disturbance Compliance Working Group report.  A summary of the frequency events is provided below:

| Date and Time | Max/Min Frequency (Hz) | Duration of Event (seconds) | Comments |
| --- | --- | --- | --- |
| 3/2/2014 7:37 | 59.857 | 22 | Unit trip with approximately 543 MW |
| 3/3/2014 7:31 | 59.895 | 5 | Unit trip with approximately 538 MW |
| 3/10/2014 8:57 | 59.877 | 96 | Two unit trips and generation deviation with approximately 957 MW lost. |
| 3/10/2014 18:29 | 59.777 | 65 | Unit trip with approximately 800 MW |
| 3/19/2014 8:41 | 59.796 | 89 | Unit trip with approximately 784 MW |

(Note: the duration of the frequency events is defined to be the time at which the frequency was outside the range of 60±0.1 Hz)

## Responsive Reserve Events

There were five events where Responsive Reserve MWs were released to SCED in March.  The events highlighted in blue were related to frequency events reported in section 2.1 above.

| Date and Time Released to SCED | Date and Time Recalled | Duration of Event | Maximum MWs Released | Comments |
| --- | --- | --- | --- | --- |
| 3/2/14 7:37:54 | 3/2/14 7:40:26 | 0:02:32 | 443.37 |  |
| 3/3/14 7:32:02 | 3/3/14 7:40:22 | 0:08:20 | 395.18 |  |
| 3/10/14 8:57:45 | 3/10/14 9:02:28 | 0:04:43 | 329.42 |  |
| 3/10/14 18:29:40 | 3/10/14 18:32:32 | 0:02:52 | 886.22 |  |
| 3/19/14 8:41:18 | 3/19/14 8:46:50 | 0:05:32 | 811.54 |  |

## Load Resource Events

There were no load resource deployment events in March.

## PMU Events

There were two synchrophasor events captured in March. Both were the result of frequency events detailed in section 2.1 above. When analyzing system disturbances, ERCOT evaluates PMU data according to industry standards. Events with an oscillating frequency of less than 1 Hz are considered to be inter-area, while higher frequencies indicate local events. Industry standards specify that damping ratio for inter-area oscillations should be 3.0% or greater. All events listed below indicate the ERCOT system met these standards and transitioned well after each disturbance.

| Date and Time | Event Type | Duration of Event | Comments |
| --- | --- | --- | --- |
| 3/10/2014 18:29:21 | Unit Trip | Approx. 159 sec | The event was caused by the loss of one unit generating 798 MW net. Following the trip, frequency dropped to 59.775 Hz. The oscillating frequency of 0.683 Hz with 9.55% damping ratio was observed. |
| 3/19/2014 08:41:02 | Unit Trip | Approx. 360 sec | The event was caused by the loss of one unit generating 770 MW net. Following the trip, frequency dropped to 59.795 Hz. The oscillating frequency of 0.752 Hz with 12.78% damping ratio was observed. |

# Reliability Unit Commitment

ERCOT reports on Reliability Unit Commitments (RUC) on a monthly basis. Commitments are reported grouped by operating day and weather zone. The total number of hours committed is the sum of the hours for all the units in the specified region. Additional information on RUC commitments can be found on the MIS secure site at Grid  Generation  Reliability Unit Commitment.

| DRUC Commitments |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Resource Location | # of Resources | Operating Day | # Hours Committed | Total MWhs | Reason for commitment |
| Coast | 1 | 3/3/2014 | 20 | 15,000 | Capacity |

| HRUC Commitments |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Resource Location | # of Resources | Operating Day | # Hours Committed | Total MWhs | Reason for commitment |
| Southern | 1 | 3/1/2014 | 24 | 7,771 | Valley Import |
| Southern | 1 | 3/2/2014 | 15 | 4,831 | Valley Import |
| Far West | 1 | 3/2/2014 | 5 | 1,201 | Capacity |
| N. Central | 1 | 3/2/2014 | 7 | 1,050 | Capacity |
| Coast | 14 | 3/3/2014 | 118 | 6,386 | Capacity |
| Coast | 1 | 3/4/2014 | 12 | 708 | Capacity |
| Southern | 1 | 3/8/2014 | 8 | 2,685 | Valley Import |
| Southern | 1 | 3/9/2014 | 2 | 86 | Valley Import and Local Congestion |
| Southern | 1 | 3/10/2014 | 4 | 172 | Valley Import |
| Southern | 2 | 3/11/2014 | 2 | 464 | Valley Import |
| Southern | 3 | 3/12/2014 | 24 | 6,448 | Valley Import |
| Southern | 1 | 3/14/2014 | 8 | 1,881 | Valley Import and Local Congestion |
| Southern | 1 | 3/15/2014 | 9 | 2,129 | Valley Import |
| Southern | 2 | 3/16/2014 | 30 | 6,898 | Valley Import |
| Southern | 2 | 3/17/2014 | 9 | 1,374 | Valley Import |
| Southern | 2 | 3/18/2014 | 29 | 8,635 | Valley Import and Local Congestion |
| Southern | 2 | 3/19/2014 | 12 | 2,798 | Valley Import |
| Southern | 1 | 3/20/2014 | 3 | 1,186 | Valley Import |
| Southern | 1 | 3/21/2014 | 25 | 9,119 | Valley Import |
| Southern | 3 | 3/22/2014 | 27 | 8,023 | Valley Import |
| Southern | 2 | 3/23/2014 | 20 | 5,256 | Valley Import |
| Southern | 2 | 3/24/2014 | 15 | 3,461 | Valley Import |
| Southern | 1 | 3/25/2014 | 6 | 2,923 | Valley Import |

# Wind Generation as a Percent of Load

# Congestion Analysis

The number of congestion events experienced by the ERCOT system remained steady again in March. Since the weather was generally milder in March, a greater fraction of the congestion events was related to outages than to cold weather, as was the case in January and February. There were also four days of activity on the Valley Import Generic Transmission Limit (GTL) resulting from planned outages in the area and five days of activity on the West to North GTL due to high wind output.

## Notable Constraints for March

Nodal protocol section 3.20 specifies that ERCOT shall identify transmission constraints that are active or binding three or more times within a calendar month. As part of this process, ERCOT reports congestion that meets this criterion to ROS. In addition ERCOT also highlights notable constraints that have an estimated congestion rent exceeding $1,000,000 for a calendar month. These constraints are detailed in the table below. Rows highlighted in blue indicate the congestion was affected by one or more outages. For a list of all constraints activated in SCED for the month of March, please see Appendix A at the end of this report.

| Contingency | Overload | # of Days Constraint Active | Estimated Congestion Rent | Transmission Project |
| --- | --- | --- | --- | --- |
| Basecase | Valley Import | 4 | $11,547,002 |  |
| DCKT Paris Switch - Valley Ses and Valley South 345 kV | Paris Switch AXFMR1 (3) 345/138 kV | 3 | $9,506,905 | 14TPIT0093 |
| Sun Switch - Morgan Creek Ses 138 kV | Snyder - Sacroc 138 kV | 1 | $6,242,688 | 09TPIT0120 |
| Lytton Springs LY_AT2 345/138 kV | Lytton Springs LY_AT1 345/138 kV | 1 | $6,207,687 |  |
| Alice - Kingsville 138 kV | Lon Hill - Calallen Sub 69 kV | 1 | $3,918,991 | 2012-R13, 12TPIT0181 |
| DCKT Watermill Switch - Desoto Switch and Cedar Hill Switch 345 kV | Sargent Road AXFMR1H (3) 345/138 kV | 1 | $3,794,589 | 11TPIT0034 |
| Paris Switch AXFMR1 (3) 345/138 kV | Forest Grove Switch - Eustace Southeast 138 KV | 1 | $3,371,396 | 17TPIT0020 |
| Nelson Sharpe - Lon Hill 345 kV | Lon Hill - Kingsville 138 kV | 3 | $3,362,732 | 16TPIT0026, 2012-R18 |
| Shamburger Switch - Martin Lake Ses 345 kV | Elkton - Tyler West 138 kV | 1 | $2,982,251 | 12TPIT0118 |
| Sacroc - Sun Switch 138 kV | Morgan Creek Ses - Sun Switch 138 kV | 1 | $2,490,202 | 15TPIT0087, 09TPIT0120 |
| North Edinburg - Lon Hill 345 kV | Rio Hondo 345_138_1 (3) 345/138 kV | 1 | $2,179,903 | 14TPIT0050, 15TPIT0024 |
| DCKT Marion - Zorn and Clear Springs 345 kV | Marion AT2 345/138 kV | 1 | $2,095,413 |  |
| DCKT Scurry County South Switch - Faraday and Long Draw 345 kV | China Grove Switch - Bluff Creek Switch 138 kV | 1 | $1,547,915 |  |
| Gaf Tnp - Greenbelt Tnp 138 kV | Greenbelt Tnp - Tejas Tnp 138 kV | 1 | $1,251,854 |  |
| Nelson Sharpe - Lon Hill 345 kV | Nelson Sharpe 138_PS | 1 | $1,232,229 | 15TPIT0024 |
| DCKT Wa Parish - Bellaire and Smithers 345 kV | Sharpstown - Bellaire 138 kV | 3 | $1,011,664 | 12TPIT0169, 14TPIT0030 |
| DCKT Scurry County South Switch - Tonkawa Switch 345 kV | Bluff Creek Switch - Exxon Sharon Ridge 138 kV | 10 | $820,973 |  |
| Laquinta - Lobo 138 kV | Bruni 138_69_1 138/69 kV | 9 | $756,819 | 11TPIT0160 |
| Nelson Sharpe - Lon Hill 345 kV | Kleberg Aep - Kingsville 138 kV | 7 | $573,109 | 13TPIT0108, 15TPIT0069 |
| Lon Hill 345_138_2 (3) 345/138 kV | Lon Hill - Smith 69 kV | 5 | $374,493 | 16TPIT0026, 2012-R18 |
| DCKT Rio Hondo - North Edinburg 345 kV and Rio - Hondo Harlingen Switch 138 kV | La Palma - Haine Drive 138 kV | 3 | $328,113 | 09TPIT0101, 14TPIT0070 |
| Victoria - Coleto Creek 138 kV (COLETO_VICTOR1) | Victoria - Coleto Creek 138 kV (COLETO_VICTOR2) | 8 | $290,036 |  |
| Ajo - Rio Hondo 345 kV | Las Pulgas - Rio Hondo 138 kV | 7 | $243,109 | 14TPIT0050 |
| Vernon 138_69T1 138/69 kV | Lake Pauline 138_69_1 138/69 kV | 3 | $147,578 |  |
| Basecase | West to North | 5 | $127,535 |  |
| Nelson Sharpe - Lon Hill 345 kV | Las Pulgas - Raymondville 2 138 kV | 3 | $71,915 | 12TPIT0103 |
| Scurry Switch - Sun Switch 138 kV | Wolfgang - Rotan 69 kV | 15 | $58,439 |  |
| Aspermont Aep - Spur 138 kV | Wolfgang - Rotan 69 kV | 8 | $35,493 |  |
| Spur - Scurry Switch 138 kV | Wolfgang - Rotan 69 kV | 4 | $7,384 |  |
| Basecase | Ena Snyder Wind - Wkn_Bkr 69 kV | 4 | $2,324 |  |

## Generic Transmission Limit Congestion

There were five days of GTL activity on the West – North stability limit resulting from high West wind output in March. In addition, there were four days of activity on the Valley Import stability limit as a result of planned outages in the area. There was no GTL activity on the North – Houston or SOP110 GTLs.

## Congestion Costs for Calendar Year 2014

The following table represents the top twenty active constraints for the calendar year to date based on the estimated congestion rent attributed to the congestion. ERCOT updates this list on a monthly basis.

| Contingency | Binding Element | # of 5-min SCED Intervals | Estimated Congestion Rent | Transmission Project |
| --- | --- | --- | --- | --- |
| Lytton Springs LY_AT2 345/138 kV | Lytton Springs LY_AT1 345/138 kV | 1,989 | $55,956,002 |  |
| Basecase | Valley Import | 495 | $11,577,259 |  |
| DCKT Gabriel - Glasscock LCRA and Rivery 138 kV, Glasscock LCRA - Gabriel 138 kV, and DCKT Gabriel - Bell County - Hutto Switch 138 kV | Marshall Ford - Lago Vista 138 kV | 209 | $9,871,526 | 15TPIT0061 |
| DCKT Paris Switch - Valley Ses and Valley South 345 kV | Paris Switch AXFMR1 (3) 345/138 kV | 1,420 | $9,291,357 | 14TPIT0093 |
| Sun Switch - Morgan Creek Ses 138 kV and Bluff Creek Switch - Ennis Creek Switch 138 kV | Snyder - Sacroc 138 kV | 153 | $6,260,965 | 09TPIT0120 |
| Alice - Kingsville 138 kV, Kingsville - Lon Hill 138 kV, Nelson Sharpe - Lon Hill 345 kV | Lon Hill - Calallen Sub 69 kV | 669 | $6,229,569 | 12TPIT0181, 2012-R13 |
| Stadium Aep - Alice 69 kV, Pawnee Switching Station - Lon Hill 345 kV, and Alice - Kingsville 138 kV | Lon Hill - Robstown Tap 69 kV | 904 | $6,091,279 | 12TPIT0180 |
| Orange Grove Switching Station - Lon Hill 138 kV and Lon Hill 345_138_2 (3) 345/138 kV | Lon Hill - Smith 69 kV | 1,762 | $4,443,063 | 16TPIT0026, 2012-R18 |
| Coleto Creek - Pawnee Switching Station 345 kV, Pawnee Switching Station - Calaveras 345 kV | Coleto Creek - Kenedy Switch 138 kV | 337 | $4,339,755 | 16TPIT0034 |
| DCKT Burleson - Carson Creek 138 kV and Pedernales - Advanced Micro Devices AEN 138 kV | Kingsberry - Mueller 138 kV | 75 | $4,036,986 | 11TPIT0008 |
| DCKT Tonkawa Switch - Scurry County South Switch 345 kV | Bluff Creek Switch - Exxon Sharon Ridge 138 kV | 2,135 | $4,004,523 |  |
| Paris Switch AXFMR1 (3) 345/138 kV, Elkton - Tyler Kelly Tire 138 kV | Forest Grove Switch - Eustace Southeast 138 KV | 192 | $3,934,733 | 17TPIT0020 |
| DCKT Watermill Switch - Desoto Switch and Cedar Hill Switch 345 kV | Sargent Road AXFMR1H (3) 345/138 kV | 186 | $3,794,589 | 11TPIT0034 |
| Pawnee Switching Station - Lon Hill 345 kV, Nelson Sharpe - Lon Hill 345 kV, North Edinburg 345_1382 345/138 kV | Nelson Sharpe - Celanese Bishop 138 kV | 1,032 | $3,562,159 | 15TPIT0024 |
| DCKT Limestone - Navarro 345 kV | Jewett - Big Brown Ses 345 kV (Line 40) | 34 | $3,428,764 |  |
| Nelson Sharpe - Lon Hill 345 kV | Lon Hill - Kingsville 138 kV | 143 | $3,362,732 | 16TPIT0026, 2012-R18 |
| Shamburger Switch - Martin Lake Ses 345 kV | Elkton - Tyler West 138 kV | 40 | $2,982,251 | 12TPIT0118 |
| Pawnee Switching Station - Lon Hill 345 kV, Nelson Sharpe - Lon Hill 345 kV, North Edinburg 345_1382 345/138 kV | Celanese Bishop - Kleberg Aep 138 kV | 1,579 | $2,871,103 | 13TPIT0108, 15TPIT0069 |
| Laquinta - Lobo 138 kV | Bruni 138_69_1 138/69 kV | 3,197 | $2,583,125 | 13TPIT0158, 13TPIT0159 |
| Sacroc - Sun Switch 138 kV | Morgan Creek Ses - Sun Switch 138 kV | 99 | $2,507,736 | 15TPIT0087, 09TPIT0120 |

# System Events

## ERCOT Peak Load

The unofficial ERCOT peak load for the month of March was 54,549 MW and occurred on March 3 during the hour ending 08:00.

## Load Shed Events

None

## Stability Events

None

## TRE/DOE Reportable Events

None

## New/Updated RAPs and PCAPs

There was one new RAP in March: Paris Switch – Valley Ses and Paris Switch – Valley South 345 kV Double Circuit Line was implemented on 3/3/2014.

## New/Modified/Removed SPS

None

## New Procedures/Forms/Operating Bulletins

| Date | Document | Description |
| --- | --- | --- |
| 3/1/2014 | Power Operations Bulletin 663 | Inadvertent Energy Procedure V1 Ver6 |
| 3/1/2014 | Power Operations Bulletin 664 | DC Tie Desk V1 Rev26 |
| 3/4/2014 | Power Operations Bulletin 665 | ERCOT DC Tie Operations Document V3 Rev8 |

# Emergency Conditions

The ERCOT Interconnection experienced fewer Emergency Conditions in March than in previous two months due to the warmer weather. In all cases, the relevant notices were posted to the ERCOT website and are summarized in the following tables.

## OCNs

None

## Advisories

| Date and Time | Description |
| --- | --- |
| 3/11/2014 13:24 | ERCOT issued an Advisory due to postponement of the DAM Solution for OD 3/12/14 due to long solution time. |
| 3/22/2014 13:31 | ERCOT issued an Advisory due to postponing the deadline for the posting of the DAM De-Energized Settlement Points in Base Case report. |

## Watches

| Date and Time | Description |
| --- | --- |
| 3/2/2014 09:00 | ERCOT issued a Watch due to a strong artic front passing through the ERCOT region. |
| 3/14/2014 14:33 | ERCOT issued a Watch due to the failure of the SCED process. |
| 3/14/2014 18:05 | ERCOT issued a Watch due to the failure of the SCED process. |

## Emergency Notices

None

# Application Performance

ERCOT system applications performed well in March. There no issues with Operations applications.

## TSAT/VSAT Performance Issues

None

## Communication Issues

None

# Net-Forecast Bias Applied to NSRS Procurement for April 2014

Each month, ERCOT calculates a net Forecast Bias pursuant to the ERCOT Ancillary Services Methodology for procurement of Non-Spinning Reserve Service (NSRS).  The table below indicates the amount of net Forecast Bias that was applied to the NSRS procurement for specified blocks of time for the month of April, 2014.

| Blocks | Negative Net Load Forecast Average Error - ERCOT | Sum of the Individual Zones | Negative Net Load Forecast Average Error - By Weather Zone for the 5 Largest Zones |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Coast | East | North Central | South Central | Southern |
| 1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 3-6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 7-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 11-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 15-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 19-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 23-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

# Appendix A: Real-Time Constraints

The following is a complete list of constraints activated in SCED for the month of March. Full contingency descriptions can be found in the Standard Contingencies List located on the MIS secure site at Grid  Generation  Reliability Unit Commitment.

| Contingency | Constrained Element | From Station | To Station | # of Days Constraint Active |
| --- | --- | --- | --- | --- |
| SSCUSUN8 | ROTN_WOLFGA1_1 | WOLFGANG | ROTN | 15 |
| DSCOTKW5 | 6216__A | BCKSW | SHRNE | 10 |
| SLAQLOB8 | BRUNI_69_1 | BRUNI | BRUNI | 9 |
| SSPUASP8 | ROTN_WOLFGA1_1 | WOLFGANG | ROTN | 8 |
| SVICCO28 | COLETO_VICTOR2_1 | COLETO | VICTORIA | 8 |
| SAJORI25 | LASPUL_RIOHON1_1 | LASPULGA | RIOHONDO | 7 |
| SN_SLON5 | KINGSV_KLEBER1_1 | KLEBERG | KINGSVIL | 7 |
| BASE CASE | W_TO_N |  |  | 5 |
| XLO2N58 | LON_HI_SMITH1_1 | LON_HILL | SMITH | 5 |
| BASE CASE | SNYDER_WKN_BK1_1 | ENAS | WKN_BKR | 4 |
| BASE CASE | VALIMP |  |  | 4 |
| SSPUMW18 | ROTN_WOLFGA1_1 | WOLFGANG | ROTN | 4 |
| DPRSVLY5 | PRSSW_MR1H | PRSSW | PRSSW | 3 |
| DRIOHAR5 | HAINE__LA_PAL1_1 | LA_PALMA | HAINE_DR | 3 |
| DWAP_BI5 | BI_ST_05_A | ST | BI | 3 |
| SN_SAJO5 | LASPUL_RAYMND1_1 | LASPULGA | RAYMND2 | 3 |
| SN_SLON5 | KINGSV_LON_HI1_1 | LON_HILL | KINGSVIL | 3 |
| XVE2R89 | PAUL_69-1 | PAUL | PAUL | 3 |
| BASE CASE | SOP110 |  |  | 2 |
| DMARZOR5 | MARION_4AT2 | MARION | MARION | 2 |
| DODEQAL5 | 6620__A | STASW | MRCAP | 2 |
| DWAP_OB5 | GT_MID90_A | GT | MID | 2 |
| SALIKIN8 | CALALS_LON_HI1_1 | LON_HILL | CALALS | 2 |
| SBOSELM5 | 1030__B | BOSQUESW | RGH | 2 |
| SMDLODE5 | 6500__B | ODEHV | BTHOT | 2 |
| SN_SLON5 | CELANE_KLEBER1_1 | CELANEBI | KLEBERG | 2 |
| SN_SLON5 | CELANE_N_SHAR1_1 | N_SHARPE | CELANEBI | 2 |
| SN_SLON5 | LOYOLA_69_1 | LOYOLA | LOYOLA | 2 |
| SSCUSUN8 | SPUR_69_1 | SPUR | SPUR | 2 |
| SSPUMW18 | SPUR_69_1 | SPUR | SPUR | 2 |
| STRIDEC8 | CKT_1027_1 | DUNLAP | DECKER | 2 |
| SWHILON5 | KINGSV_KLEBER1_1 | KLEBERG | KINGSVIL | 2 |
| XHLT89 | 6915__A | ODNTH | ODBSW | 2 |
| XPRS58 | 975__E | FGRSW | EUSSE | 2 |
| DAUSGAR5 | CKT_1027_1 | DUNLAP | DECKER | 1 |
| DAUSLOS5 | 336T405_1 | FPPYD1 | FPPYD2 | 1 |
| DCAGBRA5 | N5_P4_1 | CALAVERS | SKYLINE | 1 |
| DDUNLOS5 | 336T405_1 | FPPYD1 | FPPYD2 | 1 |
| DPRSVLY5 | PRSSW_MR1L | PRSSW | PRSSW | 1 |
| DSCOFAR5 | 6215__A | CGRSW | BCKSW | 1 |
| DSTPWHI5 | BLESSI_PALACI1_1 | BLESSING | PALACIOS | 1 |
| DTRVPIR8 | FDLGBY21_A | GBY | FDL | 1 |
| DWAP_JN5 | BI_SMR98_A | SMITHERS | BI | 1 |
| DWAP_JN5 | BI_WAP50_A | WAP | BI | 1 |
| DWH_STP5 | AIRCO4_RINCON1_1 | RINCON | AIRCO4 | 1 |
| DWTRDES5 | SARRD_MR1L | SARRD | SARRD | 1 |
| SAIRHIW9 | LON_HILL_69A2 | LON_HILL | LON_HILL | 1 |
| SAJORI25 | CELANE_N_SHAR1_1 | N_SHARPE | CELANEBI | 1 |
| SAJORI25 | MV_YUT_RAYMND1_1 | MV_YUTT | RAYMND2 | 1 |
| SBGLFRI8 | SONR_69-1 | SONR | SONR | 1 |
| SBOSWHT5 | 1030__A | ELMOT | RGH | 1 |
| SBOSWHT8 | OLKW_BOS_1 | BOSQUESW | LKWHITNY | 1 |
| SBRAUVA8 | HAMILT_MAVERI1_1 | HAMILTON | MAVERICK | 1 |
| SCALLON9 | ALICE_69A1 | ALICE | ALICE | 1 |
| SCALLON9 | LOYOLA_69_1 | LOYOLA | LOYOLA | 1 |
| SCELKLE8 | CALALS_LON_HI1_1 | LON_HILL | CALALS | 1 |
| SCNSCN38 | DEN_IND_1 | DENTON | INDUSTRL | 1 |
| SCOLBAL8 | DRSY_SANA_T1_1 | SANA_TAP | DRSY | 1 |
| SCOLPAW5 | COLETO_KENEDS1_1 | COLETO | KENEDSW | 1 |
| SCTHHA38 | SONR_69-1 | SONR | SONR | 1 |
| SECRBRA8 | 6240__A | SACRC | SNYDR | 1 |
| SECRBRA8 | ROTN_WOLFGA1_1 | WOLFGANG | ROTN | 1 |
| SELTVAN9 | RAYBURN_69_2 | RAYBURN | RAYBURN | 1 |
| SGAFGRN8 | G138_1BB_1 | GRNBELT | TEJAS | 1 |
| SGOLBRN8 | GOLDTH_9AT2 | GOLDTH | GOLDTH | 1 |
| SILLFTL8 | FDR_OZN_1 | FRIEND_R | OZNA | 1 |
| SKEYWLV8 | 6610__D | BSPSW | BSCTP | 1 |
| SKLELOY8 | LOYOLA_69_1 | LOYOLA | LOYOLA | 1 |
| SKOCNU28 | GILA_HIWAY_2_1 | GILA | HIWAY_9 | 1 |
| SLAQLOB8 | FRE_BRUN_1 | BRUNI | FREERS | 1 |
| SLORCLC9 | ABNW_ELYT1_1 | ABNW | ELYT | 1 |
| SLOSLOS5 | 336T405_1 | FPPYD1 | FPPYD2 | 1 |
| SMCFWAR9 | CALALS_LON_HI1_1 | LON_HILL | CALALS | 1 |
| SMDLODE5 | 6500__C | BTHOT | ODESW | 1 |
| SMUESPR8 | BOW_FMR1 | BOW | BOW | 1 |
| SN_SLON5 | ALICE_69A1 | ALICE | ALICE | 1 |
| SN_SLON5 | CALALS_LON_HI1_1 | LON_HILL | CALALS | 1 |
| SN_SLON5 | KINGSV_KLEBER1_1 | KINGSVIL | KLEBERG | 1 |
| SN_SLON5 | N_SHARPE_PS1 | N_SHARPE | N_SHARPE | 1 |
| SNEDLON5 | RIOHONDO_AT1L | RIOHONDO | RIOHONDO | 1 |
| SOXYIN28 | I_DUPP_I_DUPS1_1 | I_DUPP1 | I_DUPSW | 1 |
| SRODB_D8 | AIRLIN_CABANI1_1 | AIRLINE | CABANISS | 1 |
| SSACSUN8 | 6474__A | MGSES | SUNSW | 1 |
| SSACSUN8 | 6474__A | SUNSW | MGSES | 1 |
| SSCUSUN8 | GIRA_T_SPUR1_1 | SPUR | GIRA_TAP | 1 |
| SSCUSUN8 | ROBY_ROTN1_1 | ROBY | ROTN | 1 |
| SSCUSUN8 | ROBY_ROTN1_1 | ROTN | ROBY | 1 |
| SSHBMLS5 | 1000__A | ELKTN | TYWST | 1 |
| SSUNMGS8 | 6240__A | SNYDR | SACRC | 1 |
| STNSPRS8 | 1560__D | PREST | LMRTP | 1 |
| STYLEL18 | 975__C | EUSSE | EUSTC | 1 |
| STYLEL18 | 975__E | FGRSW | EUSSE | 1 |
| SWCOW2C8 | G138_18_1 | WCOLMAIN | WCOLLOCL | 1 |
| XAND89 | HLTSW_FMR1 | HLTSW | HLTSW | 1 |
| XKEN358 | 68T221_1 | VERDCR | TURTCR | 1 |
| XLY2T58 | LYTTON_S_AT1H | LYTTON_S | LYTTON_S | 1 |
| XMOS58 | 6500__B | ODEHV | BTHOT | 1 |
| XNE2D58 | HAINE__LA_PAL1_1 | LA_PALMA | HAINE_DR | 1 |
| XPRS58 | 975__D | EUSTC | MABNK | 1 |
| XSC89 | PRTTLR84_A | PRT | TLR | 1 |