## Slide 1: System Strength/Short Circuit Current Minimum Requirement
June 5, 2014

## Slide 2: Background
  In parallel with the ERCOT PREZ Study, Sharyland has been evaluating the transmission system performance in the Panhandle region, specifically:
  Including generation resources meeting Section 6.9 of the ERCOT Planning Guides
  Completed assessments for the Panhandle Region including:
      steady state voltage security
      transient voltage stability
      system strength assessments
  Issue:
      The ERCOT Panhandle region does not have synchronous generators/machines or loads, which provide system strength to the grid via short circuit current ratio (SCR)
      For wind generation control systems to work properly, a strong SCR is necessary
      Synchronous condensers can provide improved system strength to mitigate the issues – but what should be the criteria for SCR for a bus and a region?
      Criteria should apply to both Planning and Operations limits

## Slide 3: Weighted Short Circuit Ratio (WSCR)
ERCOT staff has proposed a minimum Weighted Short Circuit Ratio (WSCR) of 1.5 for the Panhandle region
  WSCR would become a default minimum criteria – but not proposed as a Protocol or Planning Guide requirement
  There are no known WSCR minimums elsewhere - Also important to differentiate between WSCR and the SCR requirements at the POI for turbine vendors
Sharyland utilized a Composite Short Circuit Ratio (CSCR) approach to evaluate “optimal” amount of synchronous condensers required for in the Panhandle
  Both CSCR and WSCR approaches observed to yield similar results
  Sharyland deems it important to investigate the “technical basis/justification” for the WSCR threshold – synchronous condenser requirements are very sensitive to the target
  Using results from system strength studies performed by Sharyland, a target of 1.2 for CSCR/WSCR seems appropriate maintain control stability and 3 GW of wind exports do not require Synchronous Condensers
  Using a 1.5 CSCR/WSCR requires 250 MW of Synchronous Condensers at 3 GW of wind exports

## Slide 4: Proposal for ROS Consideration
  ROS to assign a working group to address the following:
    Review the WSCR methodology developed by ERCOT
    Determine the appropriate target/criteria for minimum POI SCR and Regional WSCR