| PGRR Number | 028 | PGRR Title | Evaluation of Compliance with Reactive Requirements |
| --- | --- | --- | --- |

| Date | March 26, 2013 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Michael Juricek |
| E-mail Address | michael.juricek@oncor.com |
| Company | Oncor Electric Delivery |
| Phone Number | 214.743.6671 |
| Cell Number |  |
| Market Segment | Investor Owned Utility (IOU) |

Comments

Voltage conditions vary widely across the ERCOT system making the use of a single voltage range for actual operation and reactive power compliance testing difficult, if not impossible.  This is the basis for the proposed changes to the language in this PGRR.

Revised Cover Page Language

None.

Revised Proposed Guide Language

5.6.1	Evaluation of Compliance with Reactive Power Requirements

(1)	ERCOT shall evaluate whether the proposed Generation Resources are designed to comply with the Reactive Power capability and voltage control requirements as specified by the Protocols. In order to accomplish this evaluation, ERCOT will confirm that proposed Generation Resources are able to deliver Reactive Power at the Point of Interconnection (POI) without adjustment to no-load main power transformer taps or other equipment requiring the Generation Resource to come Off-Line at a high voltage range specified for the POI by ERCOT and the Transmission Service Provider (TSP).  Further, ERCOT will also confirm that with adjustment to no-load main power transformer taps or other Off-Line adjustments proposed Generation Resources are designed to provide Reactive Power at the POI at a high voltage range specified for the POI by ERCOT and the TSP.  For the evaluation, ERCOT shall consider:

(a)	“Exhibit C” (or a similar exhibit) included in the Standard Generation Interconnection Agreement (SGIA); and

(b)	The data submitted through the Resource registration process.

(2)	ERCOT will indicate whether the design of the proposed Generation Resource complies with the operational standards established in Protocol Section 3.15, Voltage Support, this Planning Guide, Nodal Operating Guides, and Other Binding Documents.  Nothing in this Section 5.6.1 shall be construed to change the Reactive Power and voltage control requirements prescribed in the Protocols.