## Slide 1: PSS/E Version 33 Dynamic Conversion
DWG
ROS June Meeting
June 5, 2014
ERCOT Met Center
Austin, TX

## Slide 2: Advantages of v33
Generic Program Enhancements
  Windows 7 Compatibility - V33.1 has been tested extensively on Windows 7 and is certified as Windows 7 compatible.
  Updates to Environment Manager to better handle Python and compiler issues.
  Updated Aspen to PSS/E converter.

## Slide 3: Improvements Related to Dynamic Studies
Improved Dynamic Engine
  Increased the number of CONs, VARs and ICONs at all size levels above 12,000 buses.
    Helpful when adding load models to the case
  All CONEC and CONET models have been “Table-ized”. Improved handling of compilation of User Defined Models
Improved Data Entry via GUI
  Copy/Paste of Models on the Dynamics Spreadsheet
Improved Data Checking
  Interactive Data Checking
    Data warnings/error can now be visualized directly on the spreadsheets and model edit dialogs. The feature is enabled/disabled on the “General” tab of the Edit>Preferences dialog.
  Updated exciter limit calculation (removed iteration with closed form calculation) for AC7B, AC8B, ESAC3A and EXAC2 models.
  Power Flow and Sequence Data Checking Report
    Two new APIs, CHECK_POWERFLOW_DATA and CHECK_SEQUENCE_DATA, can be used to create a tabular report of the checks performed on the Power Flow and Sequence data by the interactive data checking function.
    Sequence data is used in fault calculations
More support for Node Breaker Modeling
  Has a breaker tab
  There is a factor of 10 increase in the maximum number of zero impedance lines allowed at all size levels. For example, at 50,000 buses, the maximum number of zero impedance lines is increased from 2,500 to 25,000. Easier to handle an expansion of the Node Breaker Model
New Solution Parameter, MXTPSS
  MXTPSS may be used to overcome the oscillations that can occur in the automatic adjustments of tap ratio and switched shunt settings during power flow solutions. Once tap and/or switched shunts have been adjusted MXTPSS times during a solution, further adjustments are suppressed
Load Model Improvements
  Each load may be characterized as either interruptible or non-interruptible. This attribute will be utilized in a future PSS®E release.
  Native Induction Machine Model
    A native induction machine model is now in use throughout the PSS®E engine. In the RAW file the induction machine data now appears at the end of the file

## Slide 4: New Models
  ABBSVC1 – ABB SVC model used in DFW and the CREZ
  WT4G2– Generic wind turbine model representing a generator connected to the grid via a power converter (Type – 4 wind machine)
  WT4E2 – Generic electrical control model for Type 4 wind machine
  VFT1 – GE variable frequency transformer
  SVSMO (SVSMO1, SVSMO2 and SVSMO3) family of FACTs models.
  GENTPJU1 - Synchronous generator model
  HVDCPLU1 - Siemens HVDC plus model
  HYGOVRU – A Hydro-governor model
  TSTGOV1 – A frequency playback model. This model is used to measure machine response against a measured frequency input as gathered from field measurements or defined frequency inputs as found in a Grid Code.

## Slide 5: Why UDMs Are Important
Allows for modeling of new types of equipment
  FACTs devices
  Wind
  Solar
Improved accuracy of models
  Historically there have been problems with generic models accurately modeling wind farm performance
  Wind Farm User Defined models were created to overcome this deficiency
  WECC has been working on improving Wind Farm Generic Models
Resource owner needs to submit accurate model parameters
  Default parameters may or may not model a wind farm correctly
  Models taken from a wind farm of the same type may or may not model a wind farm correctly
Market Fairness
  Expensive to get a recompile of UDM
  If one generator has to pay to recompile, then all need to pay to recompile or pay to have model entered into the PSS/E library

## Slide 6: ERCOT Guides
From the Planning Guide
6.2.1 Dynamics Data Requirements for Resources
(1) A Resource Entity shall submit new or updated dynamics data in accordance with Section 5, Generation Resource Interconnection or Change Request. The Resource Entity shall provide all dynamics data as described in the Dynamics Working Group Procedural Manual. The Resource Entity shall provide an accurate and appropriate model and model parameters. Resource Entities are encouraged to use standard models to represent the Resource’s dynamic and transient capability and response. If no appropriate standard model is available, the Resource Entity shall submit a model, model documentation, and the associated model parameters to ERCOT for inclusion in simulation-ready study cases as described in the Dynamics Working Group Procedural Manual.
From the DWG Procedure Manual
3 Dynamics Data
3.1 General
3.1.1 Software
The current version of the planning software used by the DWG is PSSE version 33.

## Slide 7: Nodal Protocol
Nodal Protocol: Section 17 Market Monitoring and Data Collection
17.3.2 Data Categories and Handling Procedures
ERCOT shall develop, and refine based on experience, a detailed catalog of all data categories that it can acquire and the procedures that it will use to handle such data, including procedures for protecting Protected Information. This catalog must include documentation of the meaning of the data elements, and must be updated upon any change in systems (e.g. EMMS or settlements) that affect the data elements or interpretation of these elements.
17.3.3 Accuracy of Data Collection
(1) ERCOT shall continuously apply appropriate procedures for the accurate collection of data into the Data Warehouse and accurate communication of that data for use by the PUCT Staff and IMM. By written notice, ERCOT may require Market Participants to verify the accuracy of data previously submitted to ERCOT.
(2) ERCOT shall report to the PUCT and IMM any failure by a Market Participant to provide accurate and complete information in the manner and time requested under these Protocols, and that failure may be treated as grounds for action against the Market Participant.
(3) ERCOT shall cause to be performed an audit on a periodic basis no less than once every three years of ERCOT data, data collection, and data documentation for adequacy and accuracy. The auditor will provide recommendations to address potential areas of improvements.

## Slide 8: NERC Standards
MOD 12
R2. The Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners (specified in the data requirements and reporting procedures of MOD-013-0_R1) shall provide dynamics system modeling and simulation data to its Regional Reliability Organization(s), NERC, and those entities specified within the applicable reporting procedures identified in Reliability Standard MOD-013-0_R1. If no schedule exists, then these entities shall provide data on request (30 calendar days).

## Slide 9: Market Notice History
Conversion to v33 for Dynamic Studies primarily impacts User Defined Models (UDM) since Library models are backwards compatible
SSWG
  SSWG has been using v33 for several years
  DWG has to convert SSWG data in v33 to work in v32
Notice in August 2013
Deadline Extended to December 31
Deadline Extended again to March 31
Feb 2014, ERCOT offered model assistance to Wind Farms to switch to a Library model (previous project converted PSS/E Wind UDM to generic wind models for use in TSAT)

## Slide 10: Response Summary (As of 5/20/2014)
55% of submitted updated parameters and models (.obj or .dll) files
Category 1: No model update in the RARF
  49 Resource Entities have not provided updated UDM models for PSS/e V33.
Category 2: Partial model update in the RARF
  14 Resource Entities provided in-complete UDM models for PSS/E V33.
*A Resource Entity with multiple units can be counted in both categories.

## Slide 11: Impact to DWG Dynamic Studies
Originally wanted to conduct CY2014 in v33 last year
Postponed transition to HWLL2017
Postponed transition to FY2019 starting in Mid June
  Completion of FY2019 may be slowed down
ERCOT and DWG will review incomplete or missing data
  May be able to use old parameters on new model or models supplied by another generator
  May be able to suggest parameters from ERCOT’s TSAT Wind Model conversion project
Poor response to v33 update for UDM is troubling
  Future data requests

## Slide 12: Conclusion
Poor response to data request for v33 UDM update
Will impact DWG studies
  Substitute models/parameters will be needed for those that did not submit a v33 update or submitted an incomplete update
  Will slow down the FY2019 Case Build starting in June 16
Next steps
  ERCOT will recommend substitute models/parameters for missing v33 data based on available v33 models similar to the old v32 models or the data parameters from ERCOT’s TSAT Conversion Study
  ERCOT will update the data files used to add the wind models to the case (ini files and WindMachines33)
  Tentative finish date for data conversion activities is mid July