| NPRR Number | 562 | NPRR Title | Subsynchronous Resonance |
| --- | --- | --- | --- |
| Date |  | June 9, 2014 |  |
| Submitter’s Information |  |  |  |
| Name |  | Adrian Pieniazek |  |
| E-mail Address |  | adrian.pieniazek@nrgenergy.com |  |
| Company |  | NRG Texas Power LLC |  |
| Phone Number |  | 512-691-6208 |  |
| Cell Number |  | 512-844-9888 |  |
| Market Segment |  | Independent Generator |  |

Comments

NRG Texas Power (“NRG”) requests that PRS continue to table NPRR 562 based on the memo filed by Chairman Nelson on May 29, 2014 in Project 42079.  Chairman Nelson’s memo stated her intent to open a project to look at, among other things, problems that have arisen as part of the CREZ build-out and, specifically related to this NPRR, SSO issues.  Chairman Nelson stated:

##### “Some of the transmission lines built as part of CREZ include series compensation that has the potential to cause sub-synchronous oscillation if the series capacitors that have been installed are taken out of bypass mode. This issue is a consequence of expanding the system to access resources that are located far from load centers. This Commission needs to decide how to address the existing problem, how to avoid this problem in the future, and how to resolve the cost allocation issues of mitigating this risk.”(emphasis added)

The Chairman’s memo clearly indicates she is not only willing to address the cost allocation issues related to SSO risk, but also willing to address “the existing problem” and “how to avoid this problem in the future.”  These same three issues are what market participants and ERCOT Staff have been struggling with since SSO risk was first identified.  Market participants and ERCOT Staff have attempted to address “the existing problem” through this NPRR, “how to avoid this problem in the future” through proposed modifications to the interconnection process, and the “cost allocation issue” has already been stripped from the NPRR in order to obtain Commission input.  Since the Chairman has shown a willingness to address the SSO issue in its entirety, and since there are no immediate reliability consequences of keeping the series capacitors bypassed, NRG requests that PRS continue to table the NPRR until further direction is received from the Commission on addressing, avoiding, and allocating the costs of SSO risk.

In addition to the request to continue to table the NPRR, NRG also wishes to affirm its agreement with many of the previous comments submitted by others.  Specifically, NRG agrees with, and wishes to reemphasize below, several important concepts that Calpine and Luminant mentioned previously.

- SSO risk has been thrust upon current generation owners as a consequence of transmission expansion decisions made by others.  These generation owners should be indemnified from any harm, financial, physical, or otherwise, resulting from SSO risk.

- Since SSO risk for existing generators was created by the installation of series capacitors, it should never be acceptable to require that an existing generator be tripped to protect against SSO.  Any procedural approaches, protective devices, or other mitigation techniques used to deal with potential SSO risk should always first involve bypassing the series capacitors.

- NRG agrees with Luminant and Calpine in strongly opposing ERCOT’s proposal to “relax” the Credible Single Contingency definition by counting double circuit lines on common towers as separate contingencies.  In real-time operations, transmission planning, and even in their initial filing of this NPRR, ERCOT has consistently utilized the Credible Single Contingency definition provided by the Protocols, i.e., the “Forced Outage of a double-circuit transmission line in excess of 0.5 miles in length…”  It is inconsistent, confusing, and inappropriate for ERCOT to consider the probability of a double circuit outage as being high enough that it must operate and plan the system using double-circuits as a Credible Single Contingency, yet choose to relax this reliability criterion when addressing the risk of SSO.

At this time, and subject to change in the future, NRG agrees with many of the concepts submitted in Luminant’s May 9, 2014 comments and the proposed language submitted by Calpine on May 21, 2014.  However, these two sets of comments have not yet been synchronized, and NRG’s proposed protocol language below is an attempt to consolidate the two filings and add in NRG’s own comments.  The proposed language starts with Calpine’s May 21, 2014 version as the baseline, adds in the specific Luminant comments in which NRG is in agreement at this time, and adds in NRG’s own language.  Among the comments added by NRG is a clarification that any costs associated with a detailed SSO study shall be the responsibility of the designated TSP performing the study.

Revised Cover Page Language

None proposed at this time.

Revised Proposed Protocol Language

2.1 	DEFINITIONS

Subsynchronous Oscillation (SSO)

Coincident oscillation occurring between two or more Transmission Elements or Generation Resources at a natural harmonic frequency lower than the normal operating frequency of the ERCOT System (60 Hz), including, but not limited to, the following types of interactions:

- Subsynchronous resonance – the torsional interaction between series capacitors and turbine-generators.

- Subsynchronous torsional interaction – the interaction between active Transmission Elements (e.g. high-voltage direct current or Static Var Compensator) and turbine-generators.

- Induction generator effects – interactions involving the electrical network only between series capacitors and Generation Resources.

- Subsynchronous control interaction – the amplification of subsynchronous currents due to positive feedback between series capacitors and the control systems of certain Generation Resources.

2.2	ACRONYMS AND ABBREVIATIONS

SSO		Subsynchronous Oscillation

FIS		Full Interconnection Study

3.21	Subsynchronous Oscillation

3.21.1	Initial Identification and Evaluation of Subsynchronous Oscillation Risk

(1)	Subsynchronous Oscillation (SSO) screening studies, including frequency scans, shall be performed by ERCOT in consultation with the interconnecting Transmission Service Provider (TSP) to evaluate a Generation Resource’s risk of becoming radial or near radial to a Transmission Element  capable of causing SSO.

(2)	In the case of a new Generation Resource, ERCOT’s initial evaluation and screening studies shall occur through the ERCOT Generator Interconnection Screening study process provided in the ERCOT Planning Guide.

(3)	In the case of a change to the topology of the ERCOT Transmission Grid, ERCOT’s initial evaluation and screening studies shall occur through ERCOT’s review of transmission project proposals submitted through the ERCOT Regional Planning process pursuant to Section 3.11, Transmission Planning, and ERCOT’s review of transmission project updates.

(4)	If the screening study shows an SSO risk in the case of six or fewer concurrent Transmission Element Outages in the converged power flow case, then a detailed SSO risk study shall be performed by a designated TSP for a Generation Resource.  For all SSO studies in this Section, double-circuit transmission lines in excess of 0.5 miles in length will be studied as a single Transmission Element Outage.

(5)	If ERCOT’s review of transmission project proposals submitted through the ERCOT Regional Planning process or ERCOT’s review of transmission project updates shows an SSO risk in the case of six or fewer concurrent Transmission Element Outages in a converged power flow case, then a detailed SSO risk study shall be performed by a designated TSP for the changes to the topology of the ERCOT Transmission Grid.

(6)	If ERCOT deems a detailed SSO risk study necessary, the provision for such study shall be as follows:

(a)	The designated TSP shall be the TSP owning the series capacitor or active Transmission Element involved in the SSO risk, unless another TSP is selected to perform the study by mutual agreement of the TSPs.

(b)	If more than one TSP owns series capacitors or Transmission Elements involved in the SSO risk, the TSPs shall mutually agree on the designated TSP to perform the detailed SSO risk study.

(c)	If the TSPs do not mutually agree on a designated TSP to perform the detailed SSO risk study, then ERCOT shall select one of the TSPs owning Transmission Facilities involved in the SSO risk to perform the detailed study.

3.21.2	Detailed Subsynchronous Oscillation Studies

(1)	The designated TSP shall develop a comprehensive scope, including contingencies, for the detailed SSO risk study and distribute it to ERCOT and the  affected Resource Entities and TSPs for comment.  ERCOT shall issue its comments within ten Business Days from receipt of the study scope.

(2)	The detailed SSO risk study report shall include a survey of and recommendation for possible mitigation and protection measures if needed, as defined below in Section 3.21.3. The designated TSP may engage a third-party consultant for this assessment.

(3)	Generation Resource Data – The specificity of the study and any associated recommendations are directly related to the accuracy of the data provided regarding the Generation Resource that may be at risk of SSO.

    - Upon request from ERCOT or the designated TSP, any affected Resource Entity shall provide the data necessary to model the Generation Resource for the purpose of analyzing SSO risk, if available.

    - If the requested data is proprietary and/or confidential, beyond the reasonable control of the affected Resource Entity, or can only be obtained from a manufacturer or from another third party, a non-disclosure agreement may be executed between the manufacturer or third party and the designated TSP, its consultant, if any, and ERCOT.  Detailed modelled data obtained pursuant to a non-disclosure agreement associated with a detailed SSO risk study shall not be used for any other purpose and shall not be disclosed to outside parties.

    - Any costs associated with obtaining the Generation Resource data from a manufacturer or third party shall be the responsibility of the designated TSP performing the detailed SSO risk study

    - If data is not available from the affected Resource Entity and cannot be obtained from a manufacturer or third party, then the designated TSP or its consultant, if any, may make reasonable assumptions in the study, subject to review by ERCOT and the Resource Entity..

(4)	Transmission Equipment Data – The specificity of the study and any associated recommendations are directly related to the accuracy of the data provided regarding the Transmission Elements that may affect the risk of SSO.

    - Upon request from ERCOT or the designated TSP, any affected TSP shall provide the data necessary to model the Transmission Element for the purpose of analyzing SSO risk, if available.

    - If the requested data is proprietary and/or confidential, beyond the reasonable control of the affected TSP or can only be obtained from a manufacturer or from another third party, a non-disclosure agreement may be executed between the manufacturer or third party and the designated TSP, its consultant, if any, and ERCOT.  Detailed modelled data obtained pursuant to a non-disclosure agreement associated with a detailed SSO risk study shall not be used for any other purpose and shall not be disclosed to outside parties.

    - If data is not available from the affected TSP and cannot be obtained from a manufacturer or third party, then the designated TSP or its consultant, if any, may make reasonable assumptions in the detailed SSO risk study, subject to review by ERCOT and the affected Resource Entity.

(5)	The detailed SSO risk study shall be reviewed as follows:

(a)	The designated TSP shall present the draft detailed SSO risk study report to ERCOT, affected Resource Entities, and the affected TSPs for comment.  Where multiple Generation Resources are affected, confidential Resource data shall be redacted in the study report provided to Resource Entities.

(b)	Any questions, comments, proposed revisions, or clarifications by any affected Entity shall be made in writing to the designated TSP within 30 days after receipt of the draft detailed SSO risk study.  ERCOT may extend this review period by an additional t20 Business Days by notifying the designated TSP that it needs additional time to review the draft study report.  ERCOT Staff may request additional data from the affected TSPs and Resource Entities.  ERCOT or the affected Entities may further request that the designated TSP conduct additional analysis.

- After  considering the questions, comments, proposed revisions, or clarifications received from  affected Resource Entities, and affected TSPs, ERCOT Staff, in consultation with the affected Entities, shall deem the study complete.   The designated TSP shall issue the final detailed SSO risk study report to ERCOT, affected Resource Entities, and affected TSPs.  Where multiple Generation Resources are affected, confidential Resource data shall be redacted in the study report provided to Resource Entities.

- ERCOT may deem a detailed SSO risk study not necessary if an Interconnecting Entity and/or Resource Entity synchronizing the new Generation Resource, or TSP provide documentation stating that its equipment is protected against SSO risk.  ERCOT shall review any documentation provided with other affected Resource Entities and TSPs to determine whether further analysis is needed.

3.21.3 	Subsynchronous Oscillation Protection and Mitigation Measures

(1)	Protection and/or Mitigation measures described in this Section may be necessary as a result of a detailed SSO risk study conducted pursuant to Section 3.21.2.  For purposes of this Section, the terms “Protection” and “Mitigation” shall have the following meaning:

(a)	“Protection” shall refer to the installation and use of equipment that protects against SSO risk that does not require operator action, and that must have the capability to detect and mitigate harmful SSO conditions.  For Transmission Facilities, Protection may include harmonic filters, thyristor controls, etc.  For Generation Resources, Protection may include torsional relays, mechanical redesign, etc..

(b)	“Mitigation” shall refer to the installation and use of any equipment or the implementation of any procedure that may be used to mitigate or eliminate SSO risk.

(i)	“Structural Mitigation” shall refer to installation and use of equipment that does not require operator action, and that can automatically bypass or segment a series capacitor or Transmission Element that creates SSO risk under defined conditions for which the equipment monitors.  For Transmission Facilities, this may include Special Protection Systems (SPSs), etc.

(ii)	“Procedural Mitigation” shall refer to implementation of any procedure involving operator action that may be used to mitigate or eliminate SSO risk.  Procedural Mitigation must include Outage Coordination and Real-Time situational awareness tools (e.g., monitoring, SSR alarms, etc.), and must result in a process for bypassing or segmenting the series capacitor or Transmission Element involved in creating the SSO risk under high-risk conditions.  ERCOT and the TSP requesting an Outage, clearance, or switching action shall review such actions for possible SSO risk.

(2)	The use of Protection and Mitigation measures shall be determined by assessing the nature of the SSO risk. The number of concurrent Transmission Element Outages shall be considered an indicator of the risk.  Protection and Mitigation measures will be reviewed every time that a detailed SSO risk study shows a relevant change in topology, and Protection and Mitigation measures will be updated as needed.

(a)	For existing Transmission Facilities that create SSO risk, if 3 or fewer concurrent Transmission Element Outages would put any interconnected Generation Resource at SSO risk, the TSP that owns the series capacitors or Transmission Elements involved in creating the SSO risk shall be the Responsible Entity for installing Protection or for installing Structural Mitigation that ensures that the relevant series capacitor or Transmission Element is bypassed or segmented if any interconnected Generation Resources is two or fewer concurrent Transmission Element Outages away from experiencing SSO risk.

(b)	For proposed Transmission Facilities, if the installation of a new series capacitor or Transmission Element would put any interconnected Generation Resource at SSO risk with 3 or fewer concurrent Transmission Element Outages, the Entity introducing the new Transmission Element shall be the Responsible Entity for installing Protection on its facilities.

(c)	For proposed Generation Resources, if 3 or fewer concurrent Transmission Element Outages would put any Interconnecting Entity and/or Resource Entity synchronizing a new Generation Resource at SSO risk, the Entity introducing the new Generation Resource shall be the Responsible Entity for installing Protection on its facilities.

(d)	For both existing and proposed facilities, if 6, 5, or 4 concurrent Transmission Element Outages would put any interconnected Generation Resource at SSO risk, ERCOT will work with all affected TSPs and Resource Entities to coordinate Procedural Mitigation that will ensure that the series capacitor or Transmission Element involved in creating SSO risk is bypassed or segmented if any interconnected Generation Resource is two or fewer concurrent Transmission Element Outages away from experiencing SSO risk.

(3)	No series capacitor or Transmission Element involved in creating an SSO risk may be put into service until the applicable ERCOT-approved Protection and/or Mitigation measures are in place.

(4)	The Protection and Mitigation measures required in this Section are minimum requirements and do not preclude an affected Entity from implementing additional Protection on its own facilities.

(5)	Approval and Reporting of Protection and/or Mitigation Measures.

(a)	ERCOT shall review the final detailed SSO risk study and approve, reject or recommend modification of Protection and/or Mitigation measures with 30 days of receipt of the study.

(b)	ERCOT shall incorporate conclusions regarding SSO risk, including level of study and approved Protection and/or Mitigation measures, in its future studies or reviews for transmission planning projects.

(6)	Any proposed change to an ERCOT-approved Protection or Mitigation measure associated with SSO risk shall be submitted to all affected Entities and approved by ERCOT in writing before taking effect.  ERCOT shall approve or reject the proposed change within 90 days of notification.