Methodology for Implementing Operating Reserve Demand Curve (ORDC) to Calculate Real-Time Reserve Price Adder

Effective upon implementation of Nodal Protocol Revision Request (NPRR) 568, Real-Time Reserve Price Adder Based on Operating Reserve Demand Curve

Version _0.6

Document Revisions

| Date Approved | Version | Description | Author(s) | Approved By | Effective Date |
| --- | --- | --- | --- | --- | --- |
| 11/19/13 | 0.5 | ERCOT Board approved NPRR568, Real-Time Reserve Price Adder Based on Operating Reserve Demand Curve, and associated OBD, Methodology for Implementing Operating Reserve Demand Curve (ORDC) to Calculate Real-Time Reserve Price Adder | ERCOT | ERCOT Board | Upon system implementation of NPRR568. |
| 4/8/14 | 0.6 | Revisions proposed via NPRR598, Clarify Inputs to PRC and ORDC. | ERCOT | ERCOT Board | Upon implementation of NPRR568. |
| TBD | 0.X | Addition of reliability factor. | GDF SUEZ Energy NA |  |  |

PROTOCOL DISCLAIMER

This document describes ERCOT systems and the response of these systems to Market Participant submissions incidental to the conduct of operations in the ERCOT Texas Nodal Market and is not intended to be a substitute for the ERCOT Protocols (available at http://www.ercot.com/mktrules/nprotocols/current), as amended from time to time.  If any conflict exists between this document and the Protocols, the Protocols shall control in all respects.

Table of Contents

1.	Purpose	1

2.	Methodology for Implementing ORDC	1

2.1.	Determine VOLL	2

2.2.	Determine PBMCL	2

2.2.1.	Calculation of RS and RSNS	5

2.2.2.	Calculation of πSRS and πNSRSNS	10

2.3.	Determination of Price Adders (RTORPA and RTOFFPA)	12

3.	Methodology Revision Process	12

4.	Appendix 1: Parameters for Implementing ORDC	13

# Purpose

Protocol Section 6.5.7.3, Security Constrained Economic Dispatch, requires the ERCOT Board to approve ERCOT’s methodology for implementing the Operating Reserve Demand Curve (ORDC) to calculate the Real-Time reserve price adders.  Additionally, the ERCOT Board must approve the parameters to be used in the methodology.

For each Security-Constrained Economic Dispatch (SCED) process, ERCOT calculates a Real-Time On-Line Reserve Price Adder (RTORPA) and a Real-Time Off-Line Reserve Price Adder (RTOFFPA) based on the On-Line and Off-Line available reserves in the ERCOT System and the ORDC.  The On-Line Reserve Price Adder is added to the Real-Time Locational Marginal Prices (LMPs) to determine the Real-Time Settlement Point Prices.  The price after the addition of RTORPA to LMPs approximates the pricing outcome of Real-Time energy and Ancillary Service co-optimization since RTORPA captures the value of the opportunity cost of reserves based on the defined ORDC.  Additionally, the Real-Time Off-Line Reserve Capacity (RTOFFCAP) shall be administratively set to zero when the SCED snapshot of the Physical Responsive Capability (PRC) is less than or equal to the PRC MW at which Energy Emergency Alert (EEA) Level 1 is initiated.  An Ancillary Service imbalance Settlement is done based on Protocol Section 6.7.4, Real-Time Ancillary Service Imbalance Payment or Charge, to make Resources indifferent to the utilization of their capacity for energy or Ancillary Service reserves.

This document describes:

- the ERCOT Board-approved methodology that ERCOT uses for determining the Real-Time reserve price adders based on ORDC.

- the ERCOT Board-approved parameters for determining the Real-Time reserve price adders and effective date.

# Methodology for Implementing ORDC

The maximum price on the PBPC would be set to SWCAP + 1.  The Real-Time spot market clearing process uses the SCED application to dispatch Resources and set prices.  For each execution of SCED, the System Lambda of the power balance constraint will be determined and the ORDC will be constructed as probability of reserves falling below the minimum contingency level (PBMCL) multiplied by the difference between Value of Lost Load (VOLL) and System Lambda.  Since the System Lambda in this equation is not a fixed value and could vary for each SCED execution, the Real-Time ORDC could vary for each SCED execution as well.  In short, this approach is needed with the current rules in order to ensure that power balance is given the highest priority.  This approach, which uses a modified ORDC for each SCED execution, can result in a reserve price that is near zero and an energy price near SWCAP under scarcity conditions.

Determining the following values is a major part of implementing ORDC to calculate Real-Time Reserve Price Adder:

- VOLL;

- PBMCL, defined as the probability of reserves falling below the minimum contingency level; and

- The Real-Time On-Line Reserve Price Adder (RTORPA) and Real-Time Off-Line Reserve Price Adder (RTOFFPA).

## Determine VOLL

The VOLL is a parameter for implementing the ORDC and shall be approved by ERCOT Board.

## Determine PBMCL

The key part of the concept is the determination of the probability of reserves falling below the minimum contingency level (PBMCL).  PBMCL is derived from Loss of Load Probability curve (LOLP),which depends on many factors, including the probability of forced outages, probability of Load forecast error and probability of wind forecast error.  It could also be different for different times of the day and for different months of the year.  LOLP at a given reserve level can be interpreted as the probability of the occurrence of an event with a magnitude greater than that reserve level.  A minimum contingency level (X) is chosen in order to send an appropriate scarcity price signal to maintain reliability and stability of the system.  The PBMCL is constructed by shifting the curve to the right by the minimum contingency level (X) amount, since ERCOT is at a higher risk of shedding firm Load when reserves fall near or below the minimum contingency reserve level, and setting the value to one for reserve levels below the minimum contingency level (X).  The PBMCL curve for a given reserve level (R) is given as follows:

πR=LOLPR−X,R−X>0        1             ,R−X≤0

LOLP is determined by analyzing historic events defined as the difference between the hour-ahead forecasted reserves with the reserves that were available in Real-Time during the Operating Hour.  These events are split into twenty-four groups, comprising of four seasons and six time-of-day blocks per day.  These groups are used to determine twenty-four distinct normal probability distributions of the events, which will determine the LOLP for the corresponding season and time block.  The detailed logic for determining LOLP is described as below:

- For each Operating Hour in the study period, calculate the system-wide Hour-Ahead (HA) reserve using the snapshot of last Hourly Reliability Unit Commitment (HRUC) for the Operating Hour (at the end of Adjustment Period):

HA Reserve = RUC On-Line Gen COP HSL - (RUC Load Forecast + RUC DCTIE Load)

+ RUC Off-Line Gen COP OFFNS Responsibility + RUC On-Line Load COP Non-Spin Responsibility + RUC On-Line Load COP Reg-Up Responsibility + RUC On-Line Load COP RRS Responsibility + OFF10 from COP + OFF30 from COP

- For each SCED interval in the study period, calculate the system-wide available SCED reserve using SCED telemetry and solution as:

SCED Reserve = SCED On-Line Gen HSL-SCED Gen Base Point + SCED Off-Line Gen OFFNS Schedule + SCED On-Line Load Telemetry RRS Schedule + SCED On-Line Load Telemetry Reg-Up Responsibility + SCED On-Line Load Telemetry Non-Spin Schedule + OFF10 + OFF30

- For each Operating Hour in the study period, calculate the hourly average system-wide SCED reserve by averaging the interval SCED reserve in step 2).

- For each Operating Hour in the study period, calculate the system wide Reserve Error as:

Reserve Error = HA Reserve – SCED Reserve (Hourly Average)

- For each Operating Hour in the study period, allocate it to the corresponding season and time block. All the hours will be split into 24 distribution groups developed for the analysis based on the Season and the time of day:

- 4 Seasons of

  - Winter (Months 12,1, 2),

  - Spring (Months 3,4,5),

  - Summer (Months 6,7,8) and

  - Fall (Months 9,10,11)

- 6 time-of-day blocks each consisting of 4 hours

- Calculate the mean (μ) and standard deviation (σ) for each of the twenty-four distinct LOLP distributions using the calculated Reserve Error in step 4).  The detail results for 2011 and 2012 are illustrated in Table 1.  This hourly error is normally distributed and hence LOLP for a given value reserve level R can be calculated:

LOLPμ,σ,R=1−CDFμ,σ,R

Where CDF is the Cumulative Distribution Function of the normal distribution with mean μ and standard deviationσ.

Table 1 LOLP distributions by season and time-of-day block for 2011 and 2012

| Season | For Hours | μ | σ |
| --- | --- | --- | --- |
| Winter (Month 12, 1, 2) | 1-2 and 23-24 | 185.14 | 1217.89 |
|  | 3-6 | 76.28 | 1253.93 |
|  | 7-10 | 136.32 | 1434.64 |
|  | 11-14 | -218.26 | 1441.00 |
|  | 15-18 | -53.67 | 1349.52 |
|  | 19-22 | -183.00 | 1129.31 |
| Spring (Month 3,4,5) | 1-2 and 23-24 | 245.76 | 1174.61 |
|  | 3-6 | 460.41 | 1313.46 |
|  | 7-10 | 348.16 | 1292.36 |
|  | 11-14 | -491.91 | 1332.05 |
|  | 15-18 | -253.77 | 1382.60 |
|  | 19-22 | -436.09 | 1280.47 |
| Summer (Month 6,7,8) | 1-2 and 23-24 | 374.88 | 1503.97 |
|  | 3-6 | 1044.81 | 1252.25 |
|  | 7-10 | 339.01 | 1679.70 |
|  | 11-14 | -695.94 | 1251.05 |
|  | 15-18 | -270.54 | 1284.96 |
|  | 19-22 | -730.33 | 1331.49 |
| Fall (Month 9, 10,11) | 1-2 and 23-24 | 15.90 | 1044.88 |
|  | 3-6 | 478.97 | 1014.02 |
|  | 7-10 | 322.65 | 1036.07 |
|  | 11-14 | -473.16 | 1293.83 |
|  | 15-18 | -422.21 | 1246.49 |
|  | 19-22 | -177.76 | 1231.14 |

### Calculation of RS and RSNS

RS is the reserves from Resources participating in SCED plus the Reg-Up and RRS from Load Resources and validated Real-Time telemetered OFF10 capacity.  RSNS is equal to RS plus the reserves from Resources that are not currently available to SCED but could be available in 30 minutes.

- RS  is calculated based on SCED telemetry and solution as:

Rs = RTOLCAP = RTOLHSL – RTBP + RTCLRCAP + RTNCLRRRS - RTOLNSRS

Where

RTCLRCAP = RTCLRREG + RTCLRRRS

[NPRR568: Replace paragraph (1) above with the following upon Phase 2 implementation:] - RS is calculated based on SCED telemetry and solution as: Rs = RTOLCAP = RTOLHSL – RTBP + RTCLRCAP + RTNCLRRRS + RTOFF10 - RTOLNSRS Where RTCLRCAP = RTCLRREG + RTCLRRRS

Where

- RTOLCAP is the system total Real-Time On-Line capacity of all On-Line Resources for the SCED interval.

- RTOLHSL is the system total Real-Time telemetered High Sustained Limits (HSLs) for all Generation Resources (excluding Intermittent Renewable Resources (IRRs) other than Wind-powered Generation Resources (WGRs), nuclear Resources, Resources with a telemetered ONTEST, STARTUP, or SHUTDOWN Resource Status and Resources with telemetered net real power (in MW) less than 95% of their telemetered Low Sustained Limit (LSL)) available to SCED for the SCED interval discounted by the system wide seasonal discount factor.

- RTBP is the system total SCED Base Points for all Generation Resources (excluding all IRRs other than WGRs, other than WGRs Resources with a telemetered ONTEST, STARTUP, or SHUTDOWN Resource Status and Resources with telemetered net real power (in MW) less than 95% of their telemetered LSL) for the SCED interval discounted by the system wide seasonal discount factor.

- RTCLRCAP is the system total Real-Time capacity from Controllable Load Resources for the SCED interval.  It is the sum of telemetered Real-Time Reg-Up and RRS Ancillary Service Schedules for all Controllable Load Resources.

- RTNCLRRRS is the system total validated Real-Time telemetered RRS Ancillary Service Schedule from Load Resources other than Controllable Load Resources for the SCED interval discounted by the system wide seasonal discount factor.

[NPRR568: Insert the following upon Phase 2 implementation:] - RTOFF10 is the system total validated Real-Time reserve capacity available in ten minutes for all Resources for the SCED interval discounted by the system wide seasonal discount factor. - The telemetered OFF10 capacity shall be capped at the ERCOT-calculated maximum MW the Resource can provide in ten minutes based on the Resource asset registration information, COP and telemetry information. - For an Off-Line Generation Resource providing OFF10 capacity other than a Combined Cycle Train, ERCOT shall verify the telemetered OFF10 capacity is viable in ten minutes based on the current warmth state and the corresponding start-up time of the Resource. For a Combined Cycle Train providing OFF10 capacity, ERCOT shall verify that the transition from the current configuration to the telemetered configuration providing OFF10 capacity is viable in ten minutes based on the transition times and transition matrix communicated via Resource asset registration information and the warmth state of the current configuration.

- RTOLNSRS is the system total validated Real-Time telemetered On-Line Non-Spin Ancillary Service Schedule for all On-Line Generation Resources for the SCED interval discounted by the system wide seasonal discount factor.

- RTCLRREG is the system total validated Real-Time telemetered Reg-Up Ancillary Service Schedules from Controllable Load Resources for the SCED interval discounted by the system wide seasonal discount factor.

- RTCLRRRS is the system total validated Real-Time telemetered RRS Ancillary Service Schedules from Controllable Load Resources for the SCED interval discounted by the system wide seasonal discount factor.

- The Resource reserve discount factors are the seasonal system level parameters calculated based on average seasonal temperature and can be different for different Resource type reserves.

[NPRR568: Replace paragraph (1) above with the following upon system implementation of NPRR555:] 1) RS is calculated based on SCED telemetry and solution as: Rs = RTOLCAP = RTOLHSL – RTBP + RTCLRCAP + RTNCLRRRS - RTOLNSRS Where RTCLRCAP = RTCLRP – RTCLRLSL – RTCLRNS + RTCLRREG [NPRR568: Replace paragraph (1) above with the following upon Phase 2 implementation:] - RS is calculated based on SCED telemetry and solution as: Rs = RTOLCAP = RTOLHSL – RTBP + RTCLRCAP + RTNCLRRRS + RTOFF10 - RTOLNSRS Where RTCLRCAP = RTCLRP – RTCLRLSL – RTCLRNS + RTCLRREG. Where - RTOLCAP is the system total Real-Time On-Line reserve capacity of all On-Line Resources for the SCED interval. - RTOLHSL is the system total Real-Time telemetered High Sustained Limits (HSLs) for all Generation Resources (excluding non-Wind-powered Generation Resource (WGR) Intermittent Renewable Resources (IRRs), Nuclear Resources, Resources with a telemetered ONTEST, STARTUP, or SHUTDOWN Resource Status and Resources with telemetered net real power (in MW) less than 95% of their telemetered LSL) available to SCED for the SCED interval discounted by the system wide seasonal discount factor. - RTBP is the system total SCED Base Points for all Generation Resources (excluding all IRRs other than WGRs, nuclear Resources, Resources with a telemetered ONTEST, STARTUP, or SHUTDOWN Resource Status and Resources with telemetered net real power (in MW) less than 95% of their telemetered LSL) for the SCED interval discounted by the system wide seasonal discount factor. - RTCLRCAP is the system total Real-Time capacity from Controllable Load Resources for the SCED interval. It is the sum of SCED Base Points less the telemetered CLR LSL and Non-Spin Schedule for all Controllable Load Resources. - RTNCLRRRS is the system total validated Real-Time telemetered RRS Ancillary Service Schedule from Load Resources other than Controllable Load Resources for the SCED interval discounted by the system wide seasonal discount factor. [NPRR568: Insert the following upon Phase 2 implementation:] - RTOFF10 is the system total validated Real-Time reserve capacity available in ten minutes for all Resources for the SCED interval discounted by the system wide seasonal discount factor. - The telemetered OFF10 capacity shall be capped at the ERCOT-calculated maximum MW the Resource can provide in ten minutes based on the Resource asset registration information, COP and telemetry information. - For an Off-Line Generation Resource providing OFF10 capacity other than a Combined Cycle Train, ERCOT shall verify the telemetered OFF10 capacity is viable in ten minutes based on the current warmth state and the corresponding start-up time of the Resource. For a Combined Cycle Train providing OFF10 capacity, ERCOT shall verify that the transition from the current configuration to the telemetered configuration providing OFF10 capacity is viable in ten minutes based on the transition times and transition matrix communicated via Resource asset registration information and the warmth state of the current configuration.. - RTOLNSRS is the system total Real-Time telemetered On-Line Non-Spin Ancillary Service Schedule for all On-Line Generation Resources for the SCED interval discounted by the system wide seasonal discount factor. - RTCLRBP is the system total SCED Base Points from Controllable Load Resources for the SCED interval discounted by the system wide seasonal discount factor. - RTCLRLSL is the system total Real-Time telemetered LSL from Controllable Load Resources for the SCED interval discounted by the system wide seasonal discount factor. - RTCLRREG is the system total validated capacity from Controllable Load Resources with Primary Frequency Response (not SCED qualified) Regulation-Up Schedule discounted by the system wide seasonal discount factor. - RTCLRNS is the system total validated Real-Time telemetered Non-Spin Ancillary Service Schedules from Controllable Load Resources for the SCED interval discounted by the system wide seasonal discount factor. - The Resource reserve discount factors are the seasonal system level parameters calculated based on average seasonal temperature and can be different for different Resource type reserves.

- RSNS is calculated based on SCED telemetry and solution as

Rsns = RTOLCAP + RTOFFCAP

RTOFFCAP = RTCST30HSL + RTOFFNSHSL + RTNCLRNS + RTCLRNS + RTOLNSRS

[NPRR568: Replace paragraph (2) above with the following upon Phase 2 implementation:] - RSNS is calculated based on SCED telemetry and solution as Rsns = RTOLCAP + RTOFFCAP RTOFFCAP = RTOFF30 + RTNCLRNS + RTCLRNS + RTOLNSRS

Where

- RTOLCAP is the system total Real-Time On-Line reserve capacity of all On-Line Resources for the SCED interval.

- RTOFFCAP is the system total Real-Time Off-Line reserve capacity for the SCED interval.

- RTCST30HSL is the system total Real-Time telemetered HSLs of Generation Resources that have telemetered an OFF Resource Status and can be started from a cold temperature state in 30 minutes and discounted by the system wide seasonal discount factor.

[NPRR568: Replace the above bullet (RTCST30HSL) and sub-bullet with the following upon Phase 2 implementation:] - RTOFF30 is the system total validated Real-Time reserve capacity available in 30 minutes for all the Resources for the SCED interval discounted by the system wide seasonal discount factor. - The telemetered OFF30 capacity shall be capped at the ERCOT-calculated maximum MW the Resource can provide in 30 minutes based on the Resource asset registration information, COP and telemetry information. - For an Off-Line Generation Resource providing OFF30 capacity other than a Combined Cycle Train, ERCOT shall verify the telemetered OFF30 capacity is viable in 30 minutes based on the current warmth state and the corresponding start-up time of the Resource. For a Combined Cycle Train providing OFF30 capacity, ERCOT shall verify that the transition from the current configuration to the telemetered configuration providing OFF30 capacity is viable in 30 minutes based on the transition times and transition matrix communicated via the Resource asset registration information and the warmth state of the current configuration.

- RTNCLRNS is the system total validated Real-Time telemetered Non-Spin Ancillary Service Schedules from Load Resources other than Controllable Load Resources for the SCED interval discounted by the system wide seasonal discount factor.

- RTCLRNS is the system total validated Real-Time telemetered Non-Spin Ancillary Service Schedules from Controllable Load Resources for the SCED interval discounted by the system wide seasonal discount factor.

- RTOLNSRS is the system total validated Real-Time telemetered On-Line Non-Spin Ancillary Service Schedule for all On-Line Generation Resources for the SCED interval discounted by the system wide seasonal discount factor.

- RTOFFNSHSL is the system total telemetered HSLs of Generation Resources that have telemetered an OFFNS Resource Status and discounted by the system wide seasonal discount factor.

[NPRR568: Delete the above bullet (RTOFFNSHLS) upon Phase 2 implementation:]

- The Resource reserve discount factors are the seasonal system level parameters calculated based on average seasonal temperature and can be different for different Resource type reserves.

[NPRR568: Replace paragraph (2) above with the following upon system implementation of NPRR555:] 2) RSNS is calculated based on SCED telemetry and solution as Rsns = RTOLCAP + RTOFFCAP RTOFFCAP = RTCST30HSL + RTOFFNSHSL +RTCLRNS + RTOLNSRS [NPRR568: Replace paragraph (2) above with the following upon Phase 2 implementation:] 2) RSNS is calculated based on SCED telemetry and solution as: Rsns = RTOLCAP + RTOFFCAP RTOFFCAP = RTOFF30 + RTCLRNS + RTOLNSRS. Where - RTOLCAP is the system total Real-Time On-Line reserve capacity of all On-Line Resources for the SCED interval. - RTOFFCAP is the system total Real-Time Off-Line reserve capacity for the SCED interval. - RTCST30HSL is the system total Real-Time telemetered HSLs of Generation Resources that have telemetered an OFF Resource Status and can be started from a cold temperature state in 30 minutes and discounted by the system wide seasonal discount factor. [NPRR568: Replace the above variable (RTCST30HSL) with the following upon Phase 2 implementation:] - RTOFF30 is the system total validated Real-Time reserve capacity available in 30 minutes for all the Resources for the SCED interval discounted by the system wide seasonal discount factor. - The telemetered OFF30 capacity shall be capped at the ERCOT-calculated maximum MW the Resource can provide in 30 minutes based on the Resource asset registration information, COP and telemetry information. - For an Off-Line Generation Resource providing OFF30 capacity other than a Combined Cycle Train, ERCOT shall verify the telemetered OFF30 capacity is viable in 30 minutes based on the current warmth state and the corresponding start-up time of the Resource. For a Combined Cycle Train providing OFF30 capacity, ERCOT shall verify that the transition from the current configuration to the telemetered configuration providing OFF30 capacity is viable in 30 minutes based on the transition times and transition matrix communicated via the Resource asset registration information and the warmth state of the current configuration.. - RTCLRNS is the system total validated Real-Time telemetered Non-Spin Ancillary Service Schedules from Controllable Load Resources for the SCED interval discounted by the system wide seasonal discount factor. - RTOLNSRS is the system total validated Real-Time telemetered On-Line Non-Spin Ancillary Service Schedule for all On-Line Generation Resources for the SCED interval discounted by the system wide seasonal discount factor. - RTOFFNSHSL is the system total telemetered HSLs of Generation Resources that have telemetered an OFFNS Resource Status and discounted by the system wide discount factor. [NPRR568: Remove the following variable RTOFFNSHSL upon Phase 2 implementation:]. - The Resource reserve discount factors are the seasonal system level parameters calculated based on average seasonal temperature and can be different for different Resource type reserves.

### Calculation of πSRS and πNSRSNS

πSRS and πNSRSNS are functions that describe the PBMCL at various reserve levels.

- Calculation of Curve πSRS:

πSRS is a function of the Real-Time reserves that should be available in the first 30 minutes of the hour and is intended to capture the PBMCL for that level of reserves.  The general equation for πSRS is:

πSRS=LOLPSRS−X,RS−X>0        1                ,RS−X≤0

Where

- X in this equation is a minimum contingency level and represents a level of reserves at which ERCOT may need to begin to shed firm Load.

- LOLPS is the LOLP function for the spinning reserve.

LOLPS is different from the 60 minutes LOLP in Table 1, which is calculated based on the hourly error analysis.  The reserves are classified into two categories; those that are being provided by Resources in SCED and Load Resources providing Reg-Up and RRS and those that are being provided by Resources that are not currently available to SCED but could be made available in 30 minutes.  Since the first reserve type is available immediately, those reserves are the only ones considered to be available to respond to any event that happens in the first 30 minutes of the hour.  All reserve types are then considered to be available to respond to events that happen in the second 30 minutes of the hour.  From the hourly error analysis, a mean (μ) and standard deviation (σ) for the 60 minute LOLP are determined for each of the different seasons and time blocks.  Because the error analysis is hourly, to capture the events within the first 30 minutes for πSRS, the μ and σ needs to be scaled to reflect the 30 minute timeframe, with δ=0.5 hour:

μ'=δ∗μ=0.5μ

σ'=δδ2+1−δ2∗σ=0.707σ

So the LOLPS can be calculated based on the 60 minute LOLP as follows:

LOLPSμ',σ',R=LOLP0.5μ,0.707σ,R=1−CDF0.5μ,0.707σ,R

24 πSRS curves are developed based on the season and the time of day.

- Calculation of Curve πNSRSNS:

πNSRSNS is a function of all the Real-Time reserves that can be expected to be available with the hour and is intended to capture the PBMCL for that level of reserves adjusted by a Reliability Factor based on events that happen in an hour.  The general equation for πNSRSNS is:

πNSRSNS=LOLPRSNS−X,RSNS−X>0         1                ,RSNS−X≤0

LOLP SNS is adjusted by a Reliability Factor and can be calculated as follows:

LOLP SNS (μ} {, σ', R)= LOLP (μ' + RF, σ', R)

This is similar to πSRS but the key differences here are the types of reserves considered and the  and  that are used in calculating LOLP

- The total On-Line and Off-Line applies for the full change in net Load over the hour and there is no scaling adjustments needed for  and  in the πNSRSNS calculations from duration perspective.

- The  is shifted by Reliability Factor (RF) to reflect in prices the additional uncertainty

- Again, X in this equation is a minimum contingency level

Like πSRS, twenty-four individual curves are created for πNSRSNS.

## Determination of Price Adders (RTORPA and RTOFFPA)

Once PBMCL is determined, the Real-Time On-Line Reserve Price Adder (RTORPA) and Real-Time Off-Line Reserve Price Adder (RTOFFPA) for each SCED interval can be calculated.  RTORPA (a.k.a. PS) and RTOFFPA (a.k.a. PNS) are functions of the PBMCL at various levels of Real-Time reserves, the net value of Load curtailment, and time duration during which the reserves are available. RTORPA and RTOFFPA are determined as follows:

RTORPA=PS=v∗0.5∗πSRS+PNSRTOFFPA=PNS=v∗(1−0.5)∗πNSRSNS

wherev=max(0,VOLL−SystemLambda)RS=RTOLCAPRSNS=RTOLCAP+RTOFFCAP

Where v represents the net value of Load curtailment and is calculated as the VOLL minus the SCED System Lambda.  System Lambda is subtracted from VOLL to reflect the scarcity value of the marginal dispatch capacity and to ensure that the final cost of energy does not go above the VOLL.  The Off-Line Available Reserves (RTOFFCAP) will be set to zero when the SCED snapshot of the PRC is equal to or below the PRC MW at which EEA Level 1 is initiated

# Methodology Revision Process

Revisions to this document shall be made according to the approval process as prescribed in Protocol Section 6.5.7.3, Security Constrained Economic Dispatch.

# Appendix 1: Parameters for Implementing ORDC

The definition and values of the parameters used in implementing ORDC are as follows:

| Parameter | Definition | Unit | Value |
| --- | --- | --- | --- |
| VOLL | Value of Lost Load | $/MWh | 9000 |
| X | Minimum level at which ERCOT may need to begin shedding firm Load | MW | 2000 |