| NOGRR Number |  | NOGRR Title | Revision of Voltage Control Requirements |
| --- | --- | --- | --- |
| Date Posted |  |
| Requested Resolution | Normal |
| Nodal Operating Guide Sections Requiring Revision | 2.2.5 – Automatic Voltage Regulators 2.7 – System Voltage Profile 3.7 – Transmission Operators |
| Other Binding Documents Requiring Revision or Related Revision Requests | NPRRXX – Revision of Voltage Control Requirements |
| Revision Description | This Nodal Operating Guide Revision Request |
| Reason for Revision | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |

| Business Case |
| --- |
| Qualitative Benefits | Describe qualitative benefits Examples: satisfies regulatory requirements, data transparency enhancement, etc. |
| Quantitative Benefits | Explain in detail possible benefit calculations to support quantifiable benefits Example: change is expected to save 50 Market Participants 25 hours/week at $65/hour. |
| Impact to Market Segments | Comment on impacts to Market Segments Example: potential positive impact to Consumer Market Segment in the form of lower energy prices. |
| Other | Any other information relating to the impacts or benefits of the NOGRR. |

| Sponsor |
| --- |
| Name |  |
| E-mail Address |  |
| Company |  |
| Phone Number |  |
| Cell Number |  |
| Market Segment |  |

| Market Rules Staff Contact |
| --- |
| Name |  |
| E-Mail Address |  |
| Phone Number |  |

Proposed Guide Language Revision

2.2.5	Automatic Voltage Regulators

(1)	Generation Entities providing VSS shall operate with the unit’s Automatic Voltage Regulator (AVR) in service per Protocol Section 3.15.3 (4).

(2)	Generation Entities shall immediately notify their QSEs of any change in Automatic Voltage Regulator (AVR) status (e.g. AVR unavailability due to maintenance or failure and when the AVR returns to normal operation).  QSEs shall immediately notify ERCOT and the TO at the Point of Interconnection (POI) of any change in AVR status and shall supply AVR status logs to ERCOT upon request per Protocol Section 6.5.5.1, Changes in Resource Status.

(3)	Generation Entities shall conduct performance tests on AVRs or verify AVR performance through comparison with operational data a minimum of every five years as prescribed in item (5) of Protocol Section 8.1.1.2.1.4, Voltage Support Service (VSS) Qualification, or if equipment characteristics are knowingly modified, within 30 days of the modification.  The test reports should include the minimum and maximum excitation limiters, volts/hertz settings, gain and time constants, type of voltage regulator control function, date tested, and voltage regulator control setting.

(4)	Generation Resources shall verify excitation systems model data upon initial installation, within 30 days of performance modifications, and a minimum of five years thereafter.

(5)	Generation Resource AVR modeling information required in the ERCOT Planning Criteria shall be determined from actual Generation Resource testing described in these Operating Guides.  Within 30 days of ERCOT’s request, the results of the latest test performed shall be supplied to ERCOT and the Transmission Service Provider (TSP).

2.2.10, Generation Resource Response Time Requirements

(1) 	All Generation Resources providing VSS as described in Protocol Section 3.15, Voltage Support, shall maintain the necessary procedures and processes plus communications, telemetry, remote control, automation, and staffing in order to normally comply with the response times listed below when a VSS Dispatch Instruction as described in Protocol Section 6.5.7.7, Voltage Support Service, is given to the Generation Resource or the QSE representing a Generation Resource.  Compliance is based upon normal operating conditions where VSS Dispatch Instructions respect all equipment operating limits and other restrictions that are periodically placed on equipment.  The response time to a Dispatch Instruction shall commence with the successful receipt by the appropriate Entity.

(2)	In a Force Majeure Event, compliance with VSS Dispatch Instructions shall not be required.  TSPs and QSEs shall follow Dispatch Instructions for VSS except under those exemptions described in paragraphs (1) and (2) of Protocol Section 6.5.7.9, Compliance with Dispatch Instructions.

(3)	 The required VSS response times for Generation Resources are:

(a) For automatically switchable static VAR capable devices, when voltage or reactive measurements at the POI are outside of the limits as specified in Nodal Operating Guide Section 2.7.3.5 (7) then the response (within the operating Reactive Power capability of the Generation Resource) must be sufficient to initiate response in no more than one minute and return the measurement within the required range in no more than five minutes.

(b) Response to a VSS Dispatch Instructions from ERCOT or authorized VSS Dispatch Instructions from a TSP, within the Reactive Power capability of the Generation Resource shall be completed in no more than five minutes of the receipt of a Dispatch Instruction.

2.7, System Voltage Profile and Operational Voltage Control

2.7.1	Introduction

(1)	ERCOT shall coordinate and conduct studies with the Transmission Service Providers (TSPs) to determine the normally desired Voltage Profile as specified in item (1) of Protocol Section 3.15, Voltage Support, as published on the Market Information System (MIS) Secure Area.

(2)	ERCOT shall establish and update Voltage Profiles to maintain system voltages within established limits.

(3)	Operational voltage control activities will take place between Generation Resources and TOs or between ERCOT and QSEs to control system voltage and make adjustments around the voltages defined by the Voltage Profile. These activities follow existing Good Utility Practices for management of system voltages and reactive power.

2.7.2	Establishing and Maintaining Voltage Profile Studies

2.7.2.1	ERCOT Responsibilities

- ERCOT shall be responsible for establishing and maintaining the Voltage Profile studies.  Voltage Profile studies should use the following criteria:

- All voltage and Reactive Power limits must be based on sound engineering studies that use the appropriate Network Operations Model.  Suggested voltage limits are as follows:

- High Voltage – Less than 1.05 PU Base Case and post-contingency

- Low Voltage – Above 0.95 PU Base Case and above 0.90 PU post-contingency

- Other more restrictive voltage limits that have been provided to ERCOT.

- Transfer limits shall reflect voltage and/or reactive restrictions.

- Voltage limits shall not be violated during all normal and Credible Single Contingency conditions.

- Voltage Profiles shall be calculated twice a year, and should be posted no later than May 1st for the Summer and Fall studies, and no later than November 1st for the Winter and Spring studies.  Postings may be made on the next business day if these days fall on a weekend or holiday.

- When Voltage Profile studies identify the need for special voltage control procedures to mitigate certain contingencies, ERCOT shall communicate the study results and recommended voltage control procedures to the affected QSEs and TOs.

- ERCOT shall provide the ERCOT SSWG cases used for Voltage Profile studies to affected TO/TSPs for review.

- ERCOT shall review the SSWG cases to make sure they are consistent with the RARF data for generation resources.

2.7.2.2	TO/TSP Responsibilities

- TOs/TSPs shall review and verify their transmission data in the ERCOT SSWG cases used for Voltage Profile studies are correct and shall communicate any required SSWG case changes to ERCOT

- TOs/TSPs shall notify ERCOT of normal operating voltage limits and post-contingency voltage limits for each bus if these limits are different than ERCOT-established limits.

- TOs/TSPs must coordinate high voltage limits with affected entities in order to guarantee that the maximum continuous over-voltage of equipment is not exceeded.

- TOs/TSPs must coordinate low voltage limits with affected entities in order to prevent one TO or Generation Resource from being a burden to another TO or Generation Resource.

- Voltage violations identified by a Voltage Profile study should be reviewed with ERCOT and coordinated with other TOs as necessary to resolve the voltage violation.  If the TO is unable to resolve the voltage violation(s), the TO shall coordinate with ERCOT to develop a Special Protection System (SPS), Constraint Management Plan (CMP), or other equivalent operating plan for the associated contingency or contingencies.

2.7.2.3	QSE Responsibilities

- QSEs shall notify ERCOT and affected TO’s of any other Generation Resource equipment limitations that affect the Resource’s ability to meet the posted Voltage Profile.

2.7.2.4	Generation Resource Owner Responsibilities

    - Generation Resources that do not monitor the voltage at the POI with the TSP shall have a methodology for converting the scheduled voltage specified by the TO to the voltage point being monitored by the Generator Resource owner or QSE.

    - If a Generation Resource cannot meet the posted Voltage Profile due to an equipment limitation, it shall notify its QSE.

- Generation Resources or their QSE shall provide the minimum and maximum Reactive Power output limits to ERCOT through the RARF.  Generation Resources may allow their QSE to enter this information on their behalf.

- Generation Resources or their QSE shall provide the excitation limits for each of their Generation Resources to ERCOT through the RARF in order to insure that the equipment excitation limits are not exceeded.  Generation Resources may allow their QSE to enter this information on their behalf.

2.7.3	Real Time Operational Voltage Control

      - General Criteria

(1) General operational voltage control guidelines are

:

| Nominal Voltage | Normal Operating Limits | Emergency Operating Limits | Ideal Voltage Range |
| --- | --- | --- | --- |
| 345 | 327.75 – 362.25 | 310.5 – 379.5 | 345 – 359 |
| 138 | 131.1 – 144.9 | 124.2 – 151.8 | 138 – 144 |
| 69 | 65.55 – 72.45 | 62.1 – 75.9 | 69 – 71.5 |

(2) Transmission voltage should not exceed 105% nor fall below 95% of the nominal voltage during normal operation of the system. Exceptions may be made for transmission equipment that is designed to operate above or below these ranges.

(3) Transmission voltage during emergencies (including contingency events) should not exceed equipment over excitation ratings.

(4) Transmission voltage during emergencies (including contingency events) should not result in customer voltage exceeding or falling below prescribed limits at distribution substations on the transmission system.

- Transmission voltage post contingency should neither fall below 90% nor exceed 110% of the per-unit voltage.

- Transmission voltage post contingency should not fall below any Under Voltage Load Shedding (UVLS) set point during normal operations.

- Any transmission voltage limits other than those identified in Section 2.7.3.1  shall be communicated to ERCOT via a NOMCR.

- Any Transmission voltages that exceed normal or emergency limits should be verified to be accurate prior to taking actions if possible.

- Major transmission lines shall be kept in service during light Load as much as possible.  Lines should only be removed after all applicable reactive controls are implemented and studies show that reliability will not be degraded.

2.7.3.2	ERCOT Responsibilities

- ERCOT shall be responsible for ordering generation online necessary to regulate transmission voltage and reactive flow.

- When the voltage levels deviate from established limits, ERCOT shall take immediate steps to relieve the condition using all available reactive resources.  These steps include but are not limited to:

    - evaluating TO actions taken to relieve the condition,

    - ordering additional Generation Resources online,

    - redispatch of generation,

    - deploying additional Resources,

    - ordering static Reactive Power Resources to be put in service,

    - determining if temporary limits can be utilized,

    - developing a Constraint Management Plan, and

    - firm load shed.

- For adjustments that would require Generation Resources to operate outside the power factor range specified in Nodal Protocol, Section 3.15 (3), ERCOT may issue a VSS Dispatch Instruction to the designated QSE.

- For multi-generator busses, ERCOT may not instruct any single Generation Resource to operate beyond its CURL or URL until all Generation Resources On-Line and interconnected at the same transmission bus, have been instructed to their respective CURLs or URLs.

- ERCOT will coordinate Automatic Voltage Regulator (AVR), dynamic and static reactive device Outages to ensure adequate reactive reserves are maintained.

- ERCOT shall monitor the Automatic Voltage Regulator (AVR), as required in Protocol Section 6.5.5.1, Changes in Resource Status, to assure that it is on and operating automatically at least 98% of the time in which the QSE is providing the Reactive Power supply from Generation Resources required to provide VSS.  The percentage is calculated as:  Time (AVR is on while providing Service) / (Total Time Providing Services) (100%).

- ERCOT will maintain a performance log of QSEs acknowledgements of Voltage Support Service (VSS) Dispatch Instructions concerning scheduled voltage or scheduled Reactive output requests.

- ERCOT must be aware of the location of and availability of reactive capability;

- ERCOT shall maintain displays to monitor Voltage Profiles and reactive flows;

- ERCOT shall know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers.

2.7.3.3	TO/TSP Responsibilities

- TOs shall be responsible for directing the real time Generator Resource voltage or Reactive Power set points.  TOs will communicate directly with the entity responsible for the operation of the Generation Resource as determined by the Generation Resources; this may be either the Generation Resource or a QSE. Normal communication is to request voltage or Reactive Power be raised or lowered at a specified bus by a stated number of kV or MVAR (e.g., + 1 kV, +20 MVAR, or -1 kV, -20 MVAR).

- TOs will monitor system voltages and shall operate voltage control equipment, including, but not limited to, capacitors, reactors and transformer tap changers to maintain system voltages within the normal range of the voltage profile.

- TOs shall operate static Reactive Power Resources within their operating area as required while maintaining dynamic Reactive Reserves provided by the Generation Resource.

- TOs shall provide voltage telemetry to ERCOT for all transmission buses with a defined Voltage Profile.

- TOs shall know the status of static transmission Reactive Power resources in its operating area and shall provide such information to ERCOT.

- TOs shall know the status of automatic voltage regulators and power system stabilizers in its operating area.

- TOs will maintain a log of Voltage Support Service (VSS) Dispatch Instructions issued to Generation Resources concerning scheduled voltage or scheduled Reactive output requests.

- When the voltage levels deviate from established limits, the TO shall take immediate steps to relieve the condition using available reactive resources under its control.

(iii) During normal operating conditions, TO reactive control plans should utilize static reactive devices before predicted daily maximum Load growth or dynamic reactive Resources reach operating limits.  Static reactive devices should be managed to ensure that adequate dynamic reactive reserves are maintained at all times.

(iv) During system emergencies, TO reactive control plans should maximize the use of transmission system reactive capacity before dispatching generation or shedding Load.

(v) Voltage reduction should not be done on the transmission system unless coordinated with adjacent TOs.

2.7.3.4	QSE Responsibilities

- QSEs shall respond to VSS dispatch instructions from ERCOT and it’s TO(s) within the time requirements specified per Nodal Operating Guide, Section 2.2.10(3)(b).

- Each QSE shall meet, within established tolerances, and respond to changes in the Voltage Profile established by ERCOT subject to the stated QSE Reactive Power and actual power operating characteristic limits and voltage limits.

- QSEs will maintain a log of Voltage Support Service (VSS) Dispatch Instructions received by the QSE from ERCOT or it’s TO concerning scheduled voltage or scheduled Reactive output requests.

- If a Generation Resource changes the operation mode of a unit’s AVR, the QSE shall promptly inform ERCOT and the TO at the Point of Interconnection (POI) per Protocol Section 6.5.5.1, Changes in Resource Status, and Operating Guide Section 2.2.5.  The QSE will continuously monitor the status of their Generating Resource’s AVRs and PSSs.

- Each Generation Resource shall respond to ERCOT instructed voltage control, including exceeding its Corrected Unit Reactive Limit (CURL) or Unit Reactive Limit (URL).  If the Generation Resource cannot comply with the VSS Dispatch Instruction, the QSE shall immediately notify ERCOT per Protocol Section 6.5.7.9, Compliance with Dispatch Instructions.

2.7.3.5	Generation Resource Owner Responsibilities

- Generation Resources providing VSS must be capable of producing a defined quantity of Reactive Power to maintain a Voltage Profile established by ERCOT per Nodal Protocol Section 3.15, Voltage Support.

- Generation Resources providing VSS must meet technical requirements specified in the Nodal Protocol, Section 8.1.1.2.1.4.

- Generation Resources shall not reduce high reactive loading on individual units during abnormal conditions without the consent of ERCOT unless equipment damage is imminent.

- Generation Resources providing VSS shall operate with the unit’s AVR in service per Nodal Operating Guide Section 2.2.5.

- Generation Resources providing VSS shall maintain unit voltage ride-through requirements per Operating Guide Section 2.9 (3).

- Generations Resources will maintain a log of Voltage Support Service (VSS) Dispatch Instructions received from its QSE or its TO concerning scheduled voltage or scheduled Reactive output requests.

- Except under Force Majeure conditions or other ERCOT-permitted operation of the Generation Resource, a Generation Resource required to provide VSS shall provide either leading or lagging reactive power up to the required capability of the unit upon request from a TO or ERCOT.

- Except under Force Majeure conditions or ERCOT-permitted operation of the Generation Resource, a Generation Resource required to provide VSS shall maintain the generator voltage or Reactive Power schedule within 2% of the level instructed by the TO while operating at less than the maximum reactive capability of the Generation Resource.

- The reactive capability required must be maintained at all times that the Generation Resource is On-Line.  When a Generating Resource experiences a change that affects unit reactive limits or excitation system performance and it unable to meet the minimum reactive requirements, it shall notify its QSE, and it’s TO immediately.

- Generation Resources shall respond to VSS dispatch instructions from it’s TO within the Reactive Power capability of the Generation Resource within the time requirements specified per Nodal Operating Guide, Section 2.2.10(3)(b).  If the Generation Resource cannot comply with a VSS Dispatch Instruction, the it shall immediately notify it’s TO immediately.

2.7.4	Special Consideration for Nuclear Power Plants

In all planning studies and Real-Time operations, ERCOT and TOs shall maintain the switchyard voltage at each nuclear power plant at a value that does not violate its licensing basis with the Nuclear Regulatory Commission (NRC).  ERCOT shall notify the QSE representing a nuclear power plant of the result of any studies where the voltage at the plant switchyard cannot be adequately maintained.  ERCOT and the TO shall monitor the voltage in Real-Time.  ERCOT shall provide notice to the QSE representing the nuclear power plant of any voltage inadequacy at the plant switchyard that cannot be corrected within 30 minutes.  High and low limits on switchyard voltage at each nuclear power plant necessary to meet these requirements shall be specified in ERCOT Procedures.

Voltage Reactive Plans

- Each TO must maintain a voltage/reactive plan for normal and Emergency Conditions and shall provide this plan to ERCOT and other TOs upon request.

(i)	Control plans to maintain Voltage Profiles may include but are not limited to capacitor switching, reactor switching, auto-transformer tap changing, generator reactive dispatch, transmission line switching, and Load shedding.

#### (ii) Parameters for TO reactor and capacitor switching plan

TOs shall provide switching plans for automatically controlled reactors, capacitors, and other reactive controlled sources to ERCOT.  For manually switched reactive devices, the TO shall provide its guidelines for the operation of these devices.  These plans and guidelines shall be posted on the MIS Secure Area and must be provided in accordance with the Network Operations Model Change Request (NOMCR) or other ERCOT prescribed process. The parameters to be provided in the standard reactor and capacitor switching plan as required by Protocol Section 3.10.7.1.5, Reactors, Capacitors, and other Reactive Controlled Sources are as follows:

Device Attributes

(a)	Transmission Element name per Protocol Section 3.10.7.1, Modeling of Transmission Elements and Parameters;

(b)	Substation name; and

(c)	Schedules of device:

(i)	Time-based;

(ii)	Voltage-based;

(iii)	Load-based;

(iv)	Contingency-based;

(v)	Normal Operation;

(vi)	Emergency Operation;

(vii)	Seasonal; and

(viii)	Others as required by technology.

2.9	Voltage Ride-Through Requirements for Generation Resources

(3)	Generating Resources required to provide Voltage Support Service (VSS) shall have and maintain the following capability:

(a)	Over-excitation limiters shall be provided and coordinated with the thermal capability of the generator field winding and protective relays in order to permit short-term reactive capability that allows at least 80% of the unit design standard (ANSI C50.13-1989), as follows:

Time (seconds)		10	30	60	120

Field Voltage %		208	146	125	112

After allowing temporary field current overload, the limiter shall operate through the automatic AC voltage regulator to reduce field current to the continuous rating.  Return to normal AC voltage regulation after current reduction shall be automatic.  The over-excitation limiter shall be coordinated with the over-excitation protection so that over-excitation protection only operates for failure of the voltage regulator/limiter.

(b)	Under-excitation limiters shall be provided and coordinated with loss-of-field protection to eliminate unnecessary generating unit disconnection as a result of operator error or equipment malfunction.

3.7	Transmission Operators

(1)	Transmission Operators (TOs) shall follow ERCOT instructions related to ERCOT responsibilities:

(a)	Performing the physical operation of the ERCOT Transmission Grid, including circuit breakers, switches, voltage control equipment, protective relays, metering and Load shedding equipment;

(b)	Directing changes in the operation of transmission voltage control equipment per Operating Guide Section 2.7.3;

(c)	Managing Voltage Profiles established by ERCOT per Operating Guide Section 2.7.3; and

(d)	Taking those additional actions required to prevent an imminent Emergency Condition or to restore the ERCOT Transmission Grid to a secure state in the event of a system emergency.

9.3	ERCOT Monitoring Program

9.3.1	Transmission Control

ERCOT shall report State Estimator (SE) performance in accordance with the Protocols and the Technical Advisory Committee (TAC)-approved State Estimator Standards and post such report on the Market Information System (MIS) Secure Area.

(a)	ERCOT shall produce monthly reports describing SE convergence and valid SE solution rates as described in Protocol Section 3.10.9.2, Telemetry and State Estimator Performance Monitoring.

(b)	ERCOT shall produce monthly reports describing the MW differences between SE results and power flow results for identified congested Transmission Elements as approved by TAC.

(c)	ERCOT shall produce monthly reports describing the MW differences between the SE results and telemetry for identified congested Transmission Elements as approved by TAC.

(d)	ERCOT shall produce monthly reports describing the voltage differences between the SE results and telemetry for the most important voltage buses identified in accordance with the State Estimator Standards.

(e)	ERCOT shall produce monthly reports describing the MW differences as defined in the State Estimator Standards.

(f)	ERCOT shall produce monthly reports identifying the sum of MW flows around telemetered SE Buses as described in paragraph (5) of Protocol Section 3.10.7.5.2, Continuous Telemetry of the Real-Time Measurements of Bus Load, Voltages, Tap Position, and Flows.

9.3.9	Voltage and Reactive Control Performance Monitoring

ERCOT shall post all Voltage Profiles on the MIS Secure Area.

# Comments

Stephen will follow up with ERCOT.

I’m sure it was thought through, but you would essentially remove the gray box language in Section 9.3.9 if this gets implemented.

Additionally, I don’t know if it matters or not, but when this was written as part of NOGRR 025, Section 11 was not in place.  Depending on the makeup, they would most likely be handled like a SPS or RAP.

Check with ERCOT Market Rules on how to handle un grey boxing this language.

Is there a need for 2.7.2 h(i) and (ii)?  It appears to have gone away.

(i) Transmission systems shall be designed so that effective reactive reserves shall be available without de-energizing other Facilities or shedding Load under normal conditions;   (PGRR?)

(ii) Major transmission lines shall be kept in service during light Load as much as possible. Lines should only be removed after all applicable reactive controls are implemented and studies show that reliability will not be degraded; and

Stopped Here and will pick up on Tuesday   6/24/2014.

Need to investigate further on who is responsible party either the QSE or GR.

I recommend adding a column for normal and emergency operating limits. Stephen will suggest the actual table.

Stephen will review NP for language that addresses inaccurate SCADA data in regards to voltage readings accuracy

Open to other ways to say this, and it should be more informational rather than a requirement.  This is to address the issue raised for comment SG5.

Recommend moving this to section 9.3.9 and gray boxing.  It’s not a real time action and it is a requirement based on a report in section 9.1.9 that is gray boxed.

Don’t know how it may need to be worded or even if it has to be, but QSEs are required to notify TOs if AVR/PSS changes status. OG 2.2.5 and 2.2.6.

Do TOs need a similar requirement as ERCOT above?

ERCOT shall maintain displays to monitor Voltage Profiles and reactive flows

Is there a need for 2.7.2 h(i) and (ii)?  It appears to have gone away.

(i) Transmission systems shall be designed so that effective reactive reserves shall be available without de-energizing other Facilities or shedding Load under normal conditions;   (PGRR?)

(ii) Major transmission lines shall be kept in service during light Load as much as possible. Lines should only be removed after all applicable reactive controls are implemented and studies show that reliability will not be degraded; and

Because 2.2.10(3)(b) is a five minute requirement, the response time requirement should be on the Generation Resource from the time received..

Might be unnecessary when you consider 2.2.10(3)(b) and Protocols 6.5.7.8(2) together.

A Generation Resource provides the VSS.  Section 8 performance requirements for VSS are on the Resource Entity and the Generation Resource

Additionally, this is redundant to NP 6.5.7.7(6)

6.5.5.1 and 2.2.5 cover AVR status, not operational mode.

To make consistent with 2.2.5, but it may be easier to just modify 2.2.5.

If you keep 4, then recommend moving 4 and 5 to 2.7.3.5.

I would review and consider eliminating requirements that require you to comply with other requirements.

See above

See above

Duplicate with Protocol 3.15.3 (2)Not clear what “response to transient  (3)(b)voltage disturbance” means

Stephen Solis will investigate further.

Recommend deleting this as OG 2.2.3 already is in place to match up with the NP 3.15.3 (2) requirement.

OG

2.2.3 Response to Transient Voltage Disturbance

Generation Resources should be designed in accordance with Section 6.2, System Protective Relaying, in order to properly respond to transient voltage disturbances.

I’m not sure if it matters, but they wouldn’t receive “directly” from ERCOT, but QSE.

Same comment, don’t know how much it matters.

May need a requirement on the QSE in section above to communicate to ERCOT.

Check with ERCOT Market Rules on how to handle un grey boxing this language.

Check with ERCOT Legal with removing from grey box.