## Sheet1
Requirement |  | Resource Registration Glossary | [10 empty] | Data Validation Rules
Groups that use data element | Purpose of data element | RARF Tab | Wind | Conventional Generation (Gen) | Combined Cycle (CC) | Load Resources | Notes | Field Name | Definition / Detailed Description | Screening Study (SS) (R, C, O, A) | Full Interconnect Study (FIS) (R, C, O, A) | Full Registration (R, C, O, A) | RARF DATA FIELD | Business Rules/Basic UI validations | Field/ Tab Type | Data type | Validation Type | Source | Destination Application | Required for Screening Study (SS) | Required for Full Interconnect Study (FIS) | Required for Planning
|  | General Information - Load Resource |  |  |  | X | List | This submittal is for | Select from drop down list of reason for this submittal - New Resource Entity, Revisions, Additions, Deletions |  |  | R | This submittal is for: | Not null. Select from the list: New Resource Entity, Revision, Additions or Deletions | R | Dropdown List | B,DVB |  |  | N/A | N/A | N/A
|  | General Information - Load Resource |  |  |  | X | mm/dd/yyyy | Date Form Completed | Enter date in the format MM/DD/YYYY. |  |  | O | Date Form Completed: | Optional | O | Date | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  | N/A | N/A | N/A
|  | General Information - Load Resource |  |  |  | X |  | Resource Entity Submitting Form | Enter the name of the Resource Entity. This must be the same entity name that filed as a Resource Entity on the Standard Form Agreement. The Protocols require that a Load Acting as a Resource must also complete and submit an Application. |  |  | R | Resource Entity Submitting Form: | 1.This field is not null. 2. All should be capital letters 3.No Special characters except spaces and dashes. | R | Character | B,DVE | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0 |  | N/A | N/A | N/A
|  | General Information - Load Resource |  |  |  | X | Number | Resource Entity DUNS # | Enter the Market Participant unique identifier as registered with ERCOT for the Resource Entity (DUNS number plus 4 as assigned by ERCOT). |  |  | R | Resource Entity DUNS #: | 2. Name must match ERCOT records (SIEBEL) | R | Character | B,DVE | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk |  | N/A | N/A | N/A
|  | General Information - Load Resource |  |  |  | X | Text | Primary Contact | Enter the Primary Contact person who can address ERCOT questions regarding Resource Registration submittal. Enter the contact's name, title, phone number, email address, and fax number. |  |  | R | Printed Name: | Not null | R | Character | B,DVE | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0 |  | N/A | N/A | N/A
|  | General Information - Load Resource |  |  |  | X | Text | Title: | Enter the Title of the Primary Contact |  |  | R | Title: | Not null | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  | N/A | N/A | N/A
|  | General Information - Load Resource |  |  |  | X |  | Phone Number: | Enter the Phone Number for the Primary Contact |  |  | R | Phone Number: | Not null | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  | N/A | N/A | N/A
|  | General Information - Load Resource |  |  |  | X |  | E-mail Address: | Enter the E-mail Address for the Primary Contact |  |  | R | E-mail Address: | Not null | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  | N/A | N/A | N/A
|  | General Information - Load Resource |  |  |  | X |  | Fax Number: | Enter the Fax Number for the Primary Contact |  |  | O | Fax Number: | Optional | O | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  | N/A | N/A | N/A
|  | General Information - Load Resource |  |  |  | X | Text | Secondary Contact | Enter the Secondary Contact person who can address ERCOT questions regarding Resource Registration submittal. Enter the contact's name, title, phone number, email address, and fax number. |  |  | O | Printed Name:
|  | General Information - Load Resource |  |  |  | X | Text | Title: | Enter the Title of the Secondary Contact |  |  | O | Title:
|  | General Information - Load Resource |  |  |  | X |  | Phone Number: | Enter the Phone Number for the Secondary Contact |  |  | O | Phone Number:
|  | General Information - Load Resource |  |  |  | X |  | E-mail Address: | Enter the E-mail Address for the Secondary Contact |  |  | O | E-mail Address:
|  | General Information - Load Resource |  |  |  | X |  | Fax Number: | Enter the Fax Number for the Secondary Contact |  |  | O | Fax Number:
|  | Load Resource Information |  |  |  | X |  | Common Name for Load Resource | Enter the common name of the Load that will be acting as a resource. ( e.g.. South Gulf Refinery, etc.) |  |  | R | Common Name for Load Resource | This field is not null. Data type is character | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  | N/A | N/A | N/A
|  | Load Resource Information |  |  |  | X |  | Dispatch Asset Code (provided by ERCOT) | Enter the Dispatch Asset Code (this code will be provided by ERCOT) |  |  | R | Dispatch Asset Code (provided by ERCOT) | [6 empty] | N/A | N/A | N/A
|  | Load Resource Information |  |  |  | X |  | Physical Street Address for Point of Delivery (POD) | Physical street address for Point of Delivery. For ALRs, this is the physical address of the station that load is assigned to as provided by ERCOT. |  |  | R | Physical Street Address for Point Of Delivery (POD) | This field is not null. Data type is character | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  | N/A | N/A | N/A
|  | Load Resource Information |  |  |  | X |  | Name of City for Point of Delivery (POD) | Name of city for Point of Delivery. For ALRs, this is the city of the station that load is assigned to as provided by ERCOT. |  |  | R | Name of City for Point of Delivery (POD) | This field is not null. Data type is character | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  | N/A | N/A | N/A
|  | Load Resource Information |  |  |  | X | Y/N | Is Load Netted From Generation at ERCOT Read Gensite? | Select whether Load is netted from generation |  |  | R | Is Load Netted From Generation at ERCOT Read Gensite? | This field is not null. Select from the list :Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  | N/A | N/A | N/A
|  | Load Resource Information |  |  |  | X | Y/N | Is Load Behind a NOIE Settlement Meter Point? | Select whether Load is behind a NOIE Settlement Meter |  |  | R | Is Load Behind a NOIE Settlement Meter Point? | This field is not null. Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  | N/A | N/A | N/A
|  | Load Resource Information |  |  |  | X | List | Load Resource Type (CLR/UFR/Interruptible) | Select from drop down list the Load Resource Type - CLR, or UFR or Interruptible |  |  | R | Load Resource Type (CLR/UFR/Interruptible) | Select from the list: CLR,UFR or Interruptible. Load Resource Type is not null | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0 | EMS | N/A | N/A | N/A
|  | Load Resource Information |  |  |  | X | Y/N | If CLR, will CLR be Dynamically Scheduling? | Select only if this Load Resource is a Controllable Load Resource |  |  | C | If CLR, will CLR be Dynamically Scheduling? | Select from the list Y or N. This field is optional. This field is required for CLR and optional for other types | C/O | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  | N/A | N/A | N/A
|  | Load Resource Information |  |  |  | X | Y/N | If CLR, ability to operate as a UFR type Resource? | Select only if this Load Resource is a Controllable Load Resource |  |  | C
|  | Load Resource Information |  |  |  | X | mm/dd/yyyy | Load Resource Effective Date | Enter the date the Load became a Load Resource. For new Load Resources, this date must be a future date associated with a network operations model database load. |  |  | R | Load Resource Effective Date | This field is not null. Date format should be MM/DD/YYYY | R | Date time | B | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  | N/A | N/A | N/A
|  | Load Resource Information |  |  |  | X | mm/dd/yyyy | Load Resource Expiration Date | Enter the date the Load ceased being a Load Resource. For retiring Load Resources, this date must be a future date associated with a network operations model database load. |  |  | O | Load Resource Expiration Date | This field is optional. Date format should be MM/DD/YYYY. NA is not valid, Leave it blank if not applicable | O | Date time | B | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  | N/A | N/A | N/A
|  | Load Resource Information |  |  |  | X | All Caps | Substation Name for POD | Enter the name of the substation that supplies service to the Point of Delivery of the Load Resource. For ALRs, this is the station that load is assigned to as provided by ERCOT. |  |  | R | Substation Name for POD | This field is not null. Data type is character | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  | N/A | N/A | N/A
|  | Load Resource Information |  |  |  | X | All Caps | Substation Code for POD | Enter the TDSP substation code as provided by the TDSP. |  |  | R | Substation Code for POD | This field is not null. Data type is character | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  | N/A | N/A | N/A
|  | Load Resource Information |  |  |  | X |  | Transmission Bus POD (PTI Bus No) | Enter the transmission bus location by PTI bus number or by specifying the transmission line. (Luling to Gonzales 138KV, etc.) as provided by the TDSP. For ALRs, this is the station that load is assigned to as provided by ERCOT. |  |  | R | Transmission Bus POD (PTI Bus No) | 1.This field is not null and should be a number 2.ERCOT needs to associate each load resource to one and only one load in the network model used by State Estimator. For lack of a better source of information; the static network model load connected at this PTI bus number is what this load resource will be mapped to. Therefore there MUST be a static network model load at this PTI bus number (CIM). | R | Integer | B | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  | N/A | N/A | N/A
|  | Load Resource Information |  |  |  | X | KV | Transmission Station Voltage | Enter the transmission level voltage level of the TDSP station as provided by the TDSP. Normally this will be 69 KV or higher. between 2.4 and 138 KV. |  |  | R | Transmission Station Voltage | This field is not null and should be a number | R | Integer | B | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  | N/A | N/A | N/A
|  | Load Resource Information |  |  |  | X | All Caps | Transmission Station Load Name in Network Operations Model | Enter the Load Name as listed in the ERCOT model as provided by the TDSP. |  |  | R | Transmission Station Load Name in Network Operations Model | ALL CAPS | [5 empty] | N/A | N/A | N/A
|  | Load Resource Information |  |  |  | X | List | Meter Reading Entity (TDSP) | Enter who reads the meter and provides interval data to ERCOT. |  |  | R | Meter Reading Entity (TDSP) | This field is not null. | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  | N/A | N/A | N/A
|  | Load Resource Information |  |  |  | X | Automatic | Meter Reading Entity Duns Number | Enter the Duns number for the entity above. |  |  | R | Meter Reading Entity Duns Number | This field is not null. This is either 9 or 13 digit number. Validate with the existing record in ERCOT?? | R | Integer | B,DVE | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0 |  | N/A | N/A | N/A
|  | Load Resource Information |  |  |  | X |  | ESIID assigned to meter | ESI ID number assigned to the meter. For NOIEs, the TDSP will create a non-settlement ESI ID. |  |  | R | ESI-ID assigned to meter | This field is not null and should be a number. Data type is character | R | Character | B | Angela Moy/RARF Glossary Version 4.0 /RARF Guide version 4.0 |  | N/A | N/A | N/A
|  | Load Resource Information |  |  |  | X | Y/N | Wholesale Delivery Point? | Enter Y or N, if the point of delivery is a wholesale delivery point. |  |  | R | Wholesale Delivery Point? | This field is not null. Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  | N/A | N/A | N/A
|  | Load Resource Information |  |  |  | X | List | Load Resource Control Device | Select the type of interrupting device. (Control Technology / Interruptible Switch / Circuit Breaker) |  |  | R | Load Resource Control Device | This field is not null | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0 /RARF Guide version 4.0 |  | N/A | N/A | N/A
|  | Load Resource Information |  |  |  | X | List | ERCOT Load Zone | Select the ERCOT Load Zone from the drop down list |  |  | R | ERCOT Load Zone | This field is a required and data type is character | R | Character | B,DVB | RARF Glossary Version 4.0 /Angela Moy |  | N/A | N/A | N/A
|  | Load Resource Information |  |  |  | X | MW | Maximum POD Total Load | Maximum MW Load total |  |  | R | Maximum POD Total Load | Maximum POD Total Load must be greater than or equal to Maximum INT Load MW .This field is not null and should be a Number | R | Numeric | B,DVB | Lin Xu | MMS | N/A | N/A | N/A
|  | Load Resource Information |  |  |  | X | MW | Maximum Interruptible Load MW | Maximum MW Iinterruptible or controllable Lload total |  |  | R | Maximum Interruptible Load MW | Maximum INT Load MW must be less than or equal to Maximum POD Total Load and must be less then or equal to High Reasonability Limit .This field is not null and should be a Number | [5 empty] | N/A | N/A | N/A
|  | Load Resource Information |  |  |  | X | MW | High Reasonability Limit | The High "Out-of-Bounds" value of the interruptible or controllable load chosen by the Resource Entity and used by ERCOT for validation purposes |  |  | R | High Reasonability Limit | 1. HRL >=0 . 2. High Reasonability Limit >=HSL or MPC.This field is not null and should be a Number 3. Value must be >= LRL 4. HRL >= Maximum INT Load MW | R | Numeric | B,DVB | RARF Workshop for Load Resources/ RARF Glossary Version 4.0 /RARF Guide version 4.0/Steve Krein | EMS | N/A | N/A | N/A
|  | Load Resource Information |  |  |  | X | MW | Low Reasonability Limit | The Low "Out-of-Bounds" value of the interruptible or controllable load chosen by the Resource Entity and used by ERCOT for validation purposes |  |  | R | Low Reasonability Limit | 1. LRL should be <= HRL. LRL must be >= 0 2. Low Reasonability Limit <= LSL or LPC. This field is not null and should be a Number Note in most cases the LRL = LSL = LPC = 0 | R | Numeric | B,DVB | Angela Moy/RARF Workshop for Load Resources/ RARF Glossary Version 4.0 /RARF Guide version 4.0/Steve Krein | EMS | N/A | N/A | N/A
|  | Load Resource Information |  |  |  | X | MW/min | CLR High Reasonability Ramp Rate Limit | The High "Out-of-Bounds" ramp rate value of the controllable load chosen by the Resource Entity and used by ERCOT for validation purposes. Applies to Controllable Load Resources only |  |  | C | CLR High Reasonability Ramp Rate Limit | 1. CLR High Reasonability Ramp Rate Limit >= Low Reasonability Ramp Rate Limit. This field is conditional: Required only if Load Resource type selected is 'CLR'. Must be a positive number. This field can not be null if Load Resource type selected is 'CLR'. | C | Numeric | B,DVB | Lin Xu/kiittipong/Jamil Daouk | MMS | N/A | N/A | N/A
|  | Load Resource Information |  |  |  | X | MW/min | CLR Low Reasonability Ramp Rate Limit | The Low "Out-of-Bounds" ramp rate value of the controllable load chosen by the Resource Entity and used by ERCOT for validation purposes. Applies to Controllable Load Resources only |  |  | C | CLR Low Reasonability Ramp Rate Limit | 1. CLR LowReasonableRampRateLimit <= Emergency Downward ramp rate <= CLR HighReasonableRampRateLimit. This field is conditional: Required only if Load Resource type selected is 'CLR'. Must be a positive number. This field can not be null if Load Resource type selected is 'CLR'. | C | Numeric | B,DVB | Lin Xu/kiittipong/Jamil Daouk | MMS | N/A | N/A | N/A
|  | Load Resource Information |  |  |  | X | Y/N | Private Use Network? | Select whether Load is part of a Private Use Network |  |  | R | Private Use Network? | Select from the list: Y or N. This field is Not null | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0 |  | N/A | N/A | N/A
|  | Load Resource Parameters |  |  |  | X | List | Dispatch Asset Code | Select the Dispatch Asset Code from the drop down list as provided from the Load Resources Information tab |  |  | R | Dispatch Asset Code | [6 empty] | N/A | N/A | N/A
|  | Load Resource Parameters |  |  |  | X | hours | Minimum Interruption Time (Non-CLR) | The minimum number of consecutive hours the Resource can be deployed (between breaker open to breaker close). |  |  | C | Minimum Interruption Time | 1. Minimum Interruption Time <= Maximum Interruption Time. 2.Minimum Interruption Time >=0. This field should not be null 3.Unit of measure is hour - This number should be rounded up to the nearest whole number (can't dispatch for partial hours). Data type is Integer. 4.This Field is conditional: Required {if the Load Resource Type is 'UFR or Interruptible' } (OR) { if the Load Resource Type = 'CLR' and if the field ' If CLR, ability to operate as a UFR type Resource?' = 'Y' from the Load Resource Information Tab} | C | Integer | B,DVB | Lin Xu/kiittipong/Jamil Daouk/Scott Middleton | MMS,NMMS | N/A | N/A | N/A
|  | Load Resource Parameters |  |  |  | X | hours | Minimum Restoration Time (Non-CLR) | The minimum number of consecutive hours the Resource must remain energized (not deployed), from the time the Resource is restored from interruption and available for the next potential interruption. |  |  | C | Minimum Restoration Time | 1.Minimum Restoration Time >=0. This field should not be null. 2.Unit of measure is hour - This number should be rounded up to the nearest whole number (can't dispatch for partial hours). Data type is Integer 3.This Field is conditional: Required {if the Load Resource Type is 'UFR or Interruptible' } (OR) { if the Load Resource Type = 'CLR' and if the field ' If CLR, ability to operate as a UFR type Resource?' = 'Y' from the Load Resource Information Tab} | C | Integer | B,DVB | Lin Xu/kiittipong/Jamil Daouk/Scott Middleton | MMS,NMMS | N/A | N/A | N/A
|  | Load Resource Parameters |  |  |  | X |  | Max WEEKLY Deployments (Non-CLR) | The maximum number of times the Resource can be deployed in seven consecutive days under normal operating conditions.; |  |  | C | Max WEEKLY Deployments | 1.Max WEEKLY Deployments > =0. This field should not be null and It is an Integer. 2.This Field is conditional: Required {if the Load Resource Type is 'UFR or Interruptible' } (OR) { if the Load Resource Type = 'CLR' and if the field ' If CLR, ability to operate as a UFR type Resource?' = 'Y' from the Load Resource Information Tab} | C | Integer | B,DVB | Lin Xu/kiittipong/Scott Middleton | MMS,NMMS | N/A | N/A | N/A
|  | Load Resource Parameters |  |  |  | X | hours | Max Interruption Time (Non-CLR) | The maximum number of consecutive hours the Resource can remain deployed before it needs to be energized. |  |  | C | Max Interruption Time | 1.Max Interruption Time > 0. 2.Unit of measure is hours, with only 1 digit after decimal point 3.This Field is conditional: Required {if the Load Resource Type is 'UFR or Interruptible' } (OR) { if the Load Resource Type = 'CLR' and if the field ' If CLR, ability to operate as a UFR type Resource?' = 'Y' from the Load Resource Information Tab} | C | Numeric | B,DVB | Lin Xu/kiittipong/Jamil Daouk/Scott Middleton | MMS,NMMS | N/A | N/A | N/A
|  | Load Resource Parameters |  |  |  | X |  | Max DAILY Deployments (Non-CLR) | The maximum number of times the Resource can be deployed in a day under normal operating conditions. |  |  | C | Max DAILY Deployments | 1.Max WEEKLY Deployments > Max DAILY Deployments. 2.Maximum Daily Deployment is not null and it is an Integer 3.This Field is conditional: {Required if the Load Resource Type is 'UFR or Interruptible' } (OR) { if the Load Resource Type = 'CLR' and if the field ' If CLR, ability to operate as a UFR type Resource?' = 'Y' from the Load Resource Information Tab} | C | Integer | B,DVB | Lin Xu/kiittipong/Scott Middleton | MMS,NMMS | N/A | N/A | N/A
|  | Load Resource Parameters |  |  |  | X | MWh | Max Weekly Energy (Non-CLR) | The maximum amount of energy, in MWh, a for which the Resource can be deployed in seven consecutive days |  |  | C | Max Weekly Energy | 1.Max Weekly Energy > =0. 2.This Field is conditional: Required {if the Load Resource Type is 'UFR or Interruptible' } (OR) { if the Load Resource Type = 'CLR' and if the field ' If CLR, ability to operate as a UFR type Resource?' = 'Y' from the Load Resource Information Tab} | C | Numeric | B,DVB | Lin Xu/kiittipong/Scott Middleton | MMS,NMMS | N/A | N/A | N/A
|  | Load Resource Parameters |  |  |  | X | minutes | Minimum Notice Time (Non-CLR) | The notice time that the Resource requires before deployment (e.g., instantaneous, 30 minutes, etc.). |  |  | C | Minimum Notice Time | 1.Minimum Notice Time > =0 2.Unit of measure is hour - This number should be rounded up to the nearest whole number (can't dispatch for partial hours). Data type is Integer 3.This Field is conditional: Required {if the Load Resource Type is 'UFR or Interruptible' } (OR) { if the Load Resource Type = 'CLR' and if the field ' If CLR, ability to operate as a UFR type Resource?' = 'Y' from the Load Resource Information Tab} | C | Integer | B,DVB | Lin Xu/kiittipong/Jamil Daouk/Scott Middleton | MMS,NMMS | N/A | N/A | N/A
|  | Load Resource Parameters |  |  |  | X | hours | Max Deployment Time (CLR) | The maximum amount of time a Controllable Load Resource can be deployed before it must return to normal operating conditions. |  |  | C | Max Deployment Time | 1.Max Deployment Time > 0 2.Unit of measure is hour - This number should be rounded down to the nearest whole number (can't dispatch for partial hours). Data type is Integer | C | Integer | B,DVB | Lin Xu/kiittipong/Jamil Daouk | MMS | N/A | N/A | N/A
|  | Load Resource Parameters |  |  |  | X | MWh | Max Weekly Energy (CLR) | The maximum amount of energy a Controllable Load Resource can be deployed in seven consecutive days. |  |  | C | Max Weekly Energy | Max Weekly Energy > =0 | C | Numeric | B,DVB | Lin Xu/kiittipong | MMS | N/A | N/A | N/A
|  | Load Resource Parameters |  |  |  | X | MW | MW1 (CLR NRRC) | Normal Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C | MW Rating NRRC | 1. MW1 to MW10 are increasing MW Values. 2.MW1 can't be null, and must have value for both ramp up and ramp down | C | Numeric | B,DVB | RARF Guide Version 4.0/ Jamil Daouk | NMMS | N/A | N/A | N/A
|  | Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate1 (CLR NRRC) | Enter Normal Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C | Upward Ramprate | 1. CLR Normal Upward Ramp Rate <= CLR Emergency Upward Ramp Rate. Zero or negative ramp rate values are not allowed. Normal Up ramp rate > 0 if breakpoint is given. 2. If Load Resource Type is 'CLR/UFR' then verify thatLowReasonableRampRateLimit <= Normal Up ramp rate <= HighReasonableRampRateLimit | C | Numeric | B,DVB | Lin Xu/kiittipong | MMS,NMMS | N/A | N/A | N/A
|  | Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate1 (CLR NRRC) | Enter Normal Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C | Downward Ramprate | 1.Zero or negative ramp rate values are not allowed. CLR Normal Downward Ramp Rate <= Emergency Downward Ramp Rate. Normal Dn ramp rate > 0 if breakpoint is given 2. If Load Resource Type is 'CLR/UFR' then verify that LowReasonableRampRateLimit <= Normal Dn ramp rate <= HighReasonableRampRateLimit | C | Numeric | B,DVB | Lin Xu/kiittipong | MMS,NMMS | N/A | N/A | N/A
|  | Load Resource Parameters |  |  |  | X | MW | MW2 (CLR NRRC) | Normal Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate2 (CLR NRRC) | Enter Normal Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate2 (CLR NRRC) | Enter Normal Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW | MW3 (CLR NRRC) | Normal Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate3 (CLR NRRC) | Enter Normal Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate3 (CLR NRRC) | Enter Normal Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW | MW4 (CLR NRRC) | Normal Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate4 (CLR NRRC) | Enter Normal Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate4 (CLR NRRC) | Enter Normal Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW | MW5 (CLR NRRC) | Normal Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate5 (CLR NRRC) | Enter Normal Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate5 (CLR NRRC) | Enter Normal Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW | MW6 (CLR NRRC) | Normal Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate6 (CLR NRRC) | Enter Normal Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate6 (CLR NRRC) | Enter Normal Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW | MW7 (CLR NRRC) | Normal Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate7 (CLR NRRC) | Enter Normal Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate7 (CLR NRRC) | Enter Normal Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW | MW8 (CLR NRRC) | Normal Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate8 (CLR NRRC) | Enter Normal Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate8 (CLR NRRC) | Enter Normal Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW | MW9 (CLR NRRC) | Normal Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate9 (CLR NRRC) | Enter Normal Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate9 (CLR NRRC) | Enter Normal Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW | MW10 (CLR NRRC) | Normal Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate10 (CLR NRRC) | Enter Normal Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate10 (CLR NRRC) | Enter Normal Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW | MW1 (CLR ERRC) | Emergency Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C | MW Rating ERRC | 1.MW1 to MW10 are increasing MW Values. 2.MW1 can't be null, and must have value for both ramp up and ramp down | C | Numeric | B,DVB | Lin Xu/ Jamil Daouk | MMS,NMMS | N/A | N/A | N/A
|  | Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate1 (CLR ERRC) | Enter Emergency Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C | Upward Ramprate | CLR Normal Upward Ramp Rate <= CLR Emergency Upward Ramp Rate. Zero or negative ramp rate values are not allowed. No null values are allowed, required for each CLR. LowReasonableRampRateLimit <= Emergency Up ramp rate <= HighReasonableRampRateLimit | C | Numeric | B,DVB | Lin Xu/kiittipong | MMS,NMMS | N/A | N/A | N/A
|  | Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate1 (CLR ERRC) | Enter Emergency Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C | Downward Ramprate | Zero or negative ramp rate values are not allowed. If Load Resource Type is 'CLR/UFR' then verify that LowReasonableRampRateLimit <= Emergency Dn ramp rate <= HighReasonableRampRateLimit CLR Normal Downward Ramp Rate <= CLR Emergency Downward Ramp Rate. Zero or negative ramp rate values are not allowed. No null values are allowed, required for each CLR. | C | Numeric | B,DVB | Lin Xu/kiittipong | MMS,NMMS | N/A | N/A | N/A
|  | Load Resource Parameters |  |  |  | X | MW | MW2 (CLR ERRC) | Emergency Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate2 (CLR ERRC) | Enter Emergency Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate2 (CLR ERRC) | Enter Emergency Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW | MW3 (CLR ERRC) | Emergency Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate3 (CLR ERRC) | Enter Emergency Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate3 (CLR ERRC) | Enter Emergency Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW | MW4 (CLR ERRC) | Emergency Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate4 (CLR ERRC) | Enter Emergency Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate4 (CLR ERRC) | Enter Emergency Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW | MW5 (CLR ERRC) | Emergency Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate5 (CLR ERRC) | Enter Emergency Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate5 (CLR ERRC) | Enter Emergency Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW | MW6 (CLR ERRC) | Emergency Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate6 (CLR ERRC) | Enter Emergency Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate6 (CLR ERRC) | Enter Emergency Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW | MW7 (CLR ERRC) | Emergency Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate7 (CLR ERRC) | Enter Emergency Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate7 (CLR ERRC) | Enter Emergency Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW | MW8 (CLR ERRC) | Emergency Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate8 (CLR ERRC) | Enter Emergency Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate8 (CLR ERRC) | Enter Emergency Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW | MW9 (CLR ERRC) | Emergency Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate9 (CLR ERRC) | Enter Emergency Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate9 (CLR ERRC) | Enter Emergency Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW | MW10 (CLR ERRC) | Emergency Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Upward RampRate10 (CLR ERRC) | Enter Emergency Rate at which resource can increase MW output in MW/minute for the given output level . |  |  | C
|  | Load Resource Parameters |  |  |  | X | MW/min | Downward RampRate10 (CLR ERRC) | Enter Emergency Rate at which resource can decrease MW output in MW/minute for the given output level . |  |  | C