## Sheet1
Requirement |  | Resource Registration Glossary | [10 empty] | Data Validation Rules
Groups that use data element | Purpose of data element | RARF Tab | Wind | Conventional Generation (Gen) | Combined Cycle (CC) | Load Resources | Notes | Field Name | Definition / Detailed Description | Screening Study (SS) (R, C, O, A) | Full Interconnect Study (FIS) (R, C, O, A) | Full Registration (R, C, O, A) | RARF DATA FIELD | Business Rules/Basic UI validations | Field/ Tab Type | Data type | Validation Type | Source | Destination Application | Required for Screening Study (SS) | Required for Full Interconnect Study (FIS) | Required for Planning
|  | Unit Information | X | X | X |  | Text | Resource Site Code | Enter the Site Code established in the General and Site Information tab of the GENERAL_SITE_ESIID_Information workbook. | R | R | R
|  | Unit Information | X | X | X |  | Text | Unit Name | Enter Unit Code for the generator unit (e.g.. Cedar Bayou Plant Gen 1 is "CBYG1"). | R | R | R | Unit Name | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS | Y | Y
|  | Unit Information | X | X | X |  | Automatic | Resource Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name (e.g. CBY_CBYG1). |  |  | A | Resource Name (Unit Code/Mnemonic) | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS | N | N
|  | Unit Information | X | X | X |  | Y/N | Non Modeled Generator | Refer to ERCOT Protocol Section 2 for the definition of a Non-Modeled Generator. |  |  | R | Non_Modeled Generator | Select from the list: Y or N | R | Dropdown List | B,DVB | WCS |  | N | N
|  | Unit Information | X | X | X |  | Number | PUC Registration Number | Enter the PUCT registration number. |  |  | O | PUC Registration Number | This field is optional. Enter a Valid Number or leave it blank if not applicable | O | Integer | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  | N | N
|  | Unit Information | X | X | X |  | Number | ERCOT Interconnection Project Number | Enter the ERCOT INR number. Required for new or upgraded units. |  | C | C | ERCOT Interconnection Project Number - only new units | 1.This field is optional. Required only for new units. Enter a Valid Number or leave it blank if not applicable 2. Cross check with the data entered in the field 'This submittal is for' in General Information Tab. If the value is 'New Site' then only this field is required. | O | Character | B,DVE | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/Angela Moy |  | N | Y
IMM |  | Unit Information | X | X | X |  | Number | NERC Number | Enter NERC NCR number. Required for new units. |  |  | O | NERC Number | This field is optional. Enter a Valid Number or leave it blank if not applicable | O | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  | N | N
|  | Unit Information | X | X | X |  | Y/N | Qualifying Facility | Refer to ERCOT Protocol Section 2 for the definition of Qualifying Facility. |  |  | R | Qualifying facility | QF flag is not null. Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/kittiepong | Lodestar | N | N
| Used for modeling site to get Trans. in early | Unit Information | X | X | X |  | Date | Transmission Only MRD | Planned Point of Interconnection (POI) substation energization (backfeed) model ready date for new Resources used to plan Resource integration schedule. Proposed model load date for RE owned transmission equipment. |  |  | O | Transmission Only MRD | This field is optional. Format should be: MM/DD/YYYY | O | Date | B/DVB | WCS |  | N | N
| Used for SSWG, SPWG, DWG cases. | Unit Information | X | X | X |  | Date | Standard Generation Interconnect Agreement (SGIA) Signature Date | Enter the date the Resource signed SGIA. For NOIEs, use MOU date. |  |  | R | Standard Generation Interconnection Agreement (SGIA) Signature Date | 1) This field is not null (required). Data type must be Date. 2) Date Format must be mm/dd/yyyy 3) Generate warning if > current date. | R | Date | B/DVB | CDannunzio |  | N | N
|  | Unit Information | X | X | X |  | Date | Unit Start Date (Model Ready Date) | Planned initial energy production (synchronization) date for a new unit used to plan the resouce integration schedule. Proposed model load date for unit. Required for new units only. |  |  | O | Unit Start Date (Model Ready Date) | This field is optional. Format should be: MM/DD/YYYY |  |  |  | WCS |  | N | N
|  | Unit Information | X | X | X |  | Date | Unit Commercial Date | Enter the unit's planned commercial operations date. (used in accordance with paragraph (b) of Protocol Section 4.4.9.4.1 , Mitigated Offer Cap). After commercial operations is declared, this field should be updated with the actual commercial operations date. | R | R | R | Unit Commercial Date | This field is not null. Format should be: MM/DD/YYYY Unit Start Date should be >= Site Start Date ( Site-Information Tab) | R | Date | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar,NMMS | Y | Y
|  | Unit Information | X | X | X |  | Date | Unit Retirement Date | Enter the model ready date of expected or actual retirement. Leave blank if unknown. |  |  | O | Unit End Date | This field is optional. Format should be: MM/DD/YYYY | O | Date | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar,NMMS | N | N
|  | Unit Information | X | X | X |  | All Caps | SubStation Code/SubStation Mnemonic (POI) | Enter the interconnecting transmission station code. If you need assistance in determining the corresponding ERCOT Substation Code\Substation Mnemonic, please work with your TDSP or ERCOT. | R | R | R | SubStation Code/SubStation Mnemonic | 1) This field is not null (required). Data type must be Character. 2) This field may not have any special characters, except an underscore "_" and a dash "-" . 3 Must be <= 8 characters. Warning! Substation Code should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 4) Substation code should be in Upper case letters. Generate an error if the rule fails. | R | Character | B/DVB | CDannunzio |  | Y | Y
|  | Unit Information | X | X | X |  | kV | Voltage Level (POI) | Enter the nominal voltage level at the Point of Interconnection (e.g. 69kV, 138kV, 345kV). If you need assistance in determining the corresponding Voltage Level, please work with your TDSP or ERCOT. | R | R | R | Voltage Level | 1) This field is not null (required). Data type must be a Float. 2) If the value >= 69 it must be 69, 138, or 345. 3) The value must be > 0. | R | Float | B/DVE | CDannunzio |  | Y | Y
|  | Unit Information | X | X | X |  | Number | PTI Bus Number (POI) | Enter the PTI Bus Number at the Point of Interconnection in the planning model. If you need assistance in determining the corresponding PTI Bus Number, please work with your TDSP or ERCOT. | R | R | R | PTI Bus Number | 1) This field is not null (required). Data type must be Integer. 2) This field must be between 1 - 999,999 | R | Integer | B/DVB | CDannunzio |  | Y | Y
|  | Unit Information | X | X | X |  | List | Primary Fuel Type | AB -- Agriculture Byproducts (bagasse, straw, energy crops) BFG -- Blast-Furnace Gas BIT -- Bituminous Coal BL -- Black liquor DFO -- Distillate Fuel Oil (diesel, No1 fuel oil, No 2 fuel oil, No 4 fuel oil) GEO -- Geothermal JF -- Jet Fuel KER -- Kerosene LFG -- Landfill Gas LIG -- Lignite MSW -- Municipal Solid Waste (refuse) NA -- Not Applicable NG -- Natural Gas NUC -- Nuclear (uranium, plutonium, thorium) OBG -- Other - Biomass Gas (methane, digester gas) OBL -- Other - Biomass Liquids (ethanol, fish oil, waste alcohol, other gases) OBS -- Other - Biomass Solids (animal manure/waster, medical waste, paper pellets, paper derived fuel) OG -- Other - Gas (butane, coal processes, coke-oven coal, methanol, refinery gas) OO -- Other - Oil (butane, crude, liquid byproducts, oil waste, propane) OTH -- Other (batteries, chemicals, hydrogen pitch sulfur, misc technologies) PC -- Petroleum Coke PG -- Propane RFO -- Residual Fuel Oil (No 5 and No 6 fuel oil) STM -- Steam from other units SLW -- Sludge Waste SUB -- Sub-bituminous Coal SUN -- Solar (photovoltaic, thermal) TDF -- Tires T -- Tidal WAT -- Water (conventional, pumped storage) WDL -- Wood/Wood Waste - Liquids (red liquor, sludge wood spent sulfite liquor, other liquors) WDS -- Wood/Wood Waste - Solids (peat, railroad ties, utility poles, wood chips, other solids) WH -- Waste heat WND -- Wind WOC -- Waste / Other Coal | R | R | R | Primary Fuel Type | Select from the list: AB, BFG, BIT, BL, DFO, GEO, JF, KER, LFG, LIG, MSW, NA, NG, NUC, OBG, OBL, OBS, OG, OO, OTH, PC, PG, RFO, SLW, STM, SUB, SUN, T, TDF, WAT, WDL, WDS, WH, WOC This field is not null. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS | Y | Y
|  | Unit Information | X | X | X |  | List | Secondary Fuel Type | Same data entry elements as primary fuel type, but for secondary or start-up fuel. | R | R | R | Secondary Fuel Type | Select from the list: AB, BFG, BIT, BL, DFO, GEO, JF, KER, LFG, LIG, MSW, NA, NG, NUC, OBG, OBL, OBS, OG, OO, OTH, PC, PG, RFO, SLW, STM, SUB, SUN, T, TDF, WAT, WDL, WDS, WH, WOC. This field is not null. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS | Y | Y
|  | Unit Information | X | X | X |  | List | Fuel Transportation Type | CV -- Conveyor PL -- Pipeline RR -- Railroad TK -- Truck NA -- Not Applicable |  |  | R | Fuel Transportation Type | Select from the list: CV, PL, RR, TK, NA. This field is not null. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  | N | N
|  | Unit Information | X | X | X |  | List | Resource Category | Nuclear Hydro Coal and Lignite Combined Cycle ≤ 90 MW* Combined Cycle > 90 MW* Gas Steam - Supercritical Boiler Gas Steam - Reheat Boiler Gas Steam - Non-reheat or Boiler without air-preheater Simple Cycle ≤ 90 MW Simple Cycle > 90 MW Diesel Renewable Reciprocating Engine Solar Power Storage Other |  |  | R | Resource Category | 1)Resource Category is not null. 2)Select from the list: Nuclear,Hydro,Coal and Lignite, Gas Steam- Super Critical Boiler, Gas Steam- Reheat Boiler, Gas Steam - Non Reheat or Boiler without air preheated, Simple Cycle <= 90 MW, Simple Cycle > 90 MW, Reciprocating Engine, Solar, Power Storage, Other | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms/kittiepong |  | N | N
|  | Unit Information | X | X | X |  | Y/N | Renewable | Indicate if the unit is a Renewable Energy Credit (REC) generator, as certified with the PUCT. |  |  | R | Renewable | Renewable Flag is not null. Select from the list: Y or N | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | EMS,Lodestar | N | N
|  | Unit Information | X | X | X |  | Y/N | Renewable/Offset | REC offset generators that produce generation to cover offsets they have been approved to provide, as certified with the PUCT. |  |  | R | Renewable/Offset | Select from the list : RN, OS, NA. This field is not null. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar | N | N
|  | Unit Information | X | X | X |  | List | Physical Unit Type | CA -- Combined cycle steam turbine part (includes steam part of integrated coal gasification combined cycle) CC -- Combined cycle total unit (use only for plants/generators that are in planning stage, for which specific generator details cannot be provided) CE -- Compressed air energy storage CS -- Combined cycle single shaft (combustion turbine and steam turbine share a single generator) CT -- Combined cycle combustion/gas turbine part (includes comb. turbine part of integrated coal gasification combined cycle) FC -- Fuel Cell GT -- Simple-cycle Combustion (gas) turbine (includes jet engine design) HY -- Hydraulic turbine (includes turbines associated with delivery of water by pipeline IC -- Internal combustion (diesel, piston) engine NA -- Unknown at this time (planned units only) OT -- Other PS -- Hydraulic Turbine - Reversible (pumped storage) PV -- Photovoltaic ST -- Steam Turbine including nuclear, geothermal and solar. Does not include combined cycle. WT -- Wind Turbine | R | R | R | Physical Unit Type | Select from the list: CA, CE, CS, CT, FC, GT, HY, IC, NA, OT, PS, PV, ST. This field is not null. | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  | Y | Y
|  | Unit Information | X | X | X |  | MVA | Name Plate Rating | Manufacturer designed Name Plate MVA Rating of this unit at its rated power factor (gross). | R | R | R | Name Plate Rating | Name Plate Rating should be >= Real Power Rating | R | Numeric | B,DVB | Lin Xu | EMS,MMS,NMMS | Y | Y
|  | Unit Information | X | X | X |  | MW | Real Power Rating | Maximum rated Manufacturer designed MW at rated power factor (gross). | R | R | R | Real Power Rating | Real Power Rating should be > Reactive Power Rating | R | Numeric | B,DVB | Lin Xu | MMS,NMMS | Y | Y
|  | Unit Information | X | X | X |  | MVAr | Reactive Power Rating | Manufacturer designed Maximum MVAr at rated power factor (gross) | R | R | R | Reactive Power Rating | Name Plate Rating should be >= Reactive Power Rating | R | Numeric | B,DVB | Lin Xu | MMS,NMMS | Y | Y
|  | Unit Information | X | X | X |  | MW | Turbine Rating | Maximum gross Manufacturer designed MW of the turbine (gross) | RC | RC | RC | Turbine Rating | This field is optional. Enter Numeric value or leave it blank if not applicable. | O | Numeric | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms |  | Y | Y
|  | Unit Information | X | X | X |  | kV | Unit Generating Voltage | Terminal voltage of generating unit. (equivalent to low side of GSU) | R | R | R | Unit Generating Voltage | 1. This field is not null and it should be a number 2. Unit Generating voltage can not be below 4.16 KV | R | Numeric | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | NMMS | Y | Y
|  | Unit Information | X | X | X |  | % | Governor Droop Settings | The percent change in nominal frequency that will cause generator output to change from no Load to full Load. (e.g. for 5%, use .05) |  |  | C | Governor Droop Setting | 1) This field is required 2) Data type must be Numeric, Positive value (>=0.0) 3) Generate an Error Warning if it is <(less than).02 OR >(greater than).05) | O | Numeric | B,DVB | Operation Analysis |  | N | N
|  | Unit Information | X | X | X |  | Hz | Goverrnor Dead-band | The maximum Hz deviation of system frequency (+/-) that produces no turbine Governor response, and therefore, no frequency (speed) regulation. The range of deviations of system frequency (+/-) that produces no Primary Frequency Response. |  |  | R | Governor Dead-band | 1) This field is required 2) Data type must be Numeric, Positive value (>=0.0) 3) Generate an Error if > 0.036. | R | Numeric | B,DVB | Operation Analysis |  | N | N
|  | Unit Information | X | X | X |  | degree F | Design Max Ambient Temperature | This is the plant design maximum (high) air temperature. |  |  | O | Design Max Ambient Temperature | 1) If a numeric value is entered, then the Value must >100 and <150 2) “NA” 3) “Unknown” |  |  |  | Operation Analysis |  | N | N
|  | Unit Information | X | X | X |  | degree F | Design Min Ambient Temperature | This is the plant design minimum (low) air temperature. |  |  | O | Design Min Ambient Temperature | 1) If a numeric value is entered, then the Value must >-100 and <32 2) “NA” 3) “Unknown” |  |  |  | Operation Analysis |  | N | N
|  | Unit Information | X | X | X |  | decimal degrees (N) | Latitude of Center of Plant | The geographic coordinate that specifies the north-south position of the plant provided in decimal degrees | R | R | R | Latitude Of Center Of Plant | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if Latitude < 25.0 or > 37.0. | [5 empty] | Y | Y
|  | Unit Information | X | X | X |  | decimal degrees (W) | Longitude of Center of Plant | The geographic coordinate that specifies the east-west position of the plant provided in decimal degrees | R | R | R | Longitude Of Center Of Plant | 1) This field is required 2) Data type must be real 3) Generate an Error if blank. Generate Warning if <93 or > 107 . | [5 empty] | Y | Y
|  | Ownership | X | X |  |  | List | Unit Name | Code for name of generator unit, as provided on the Unit Information Train tab. |  |  | R | Unit Name | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS | N | N
|  | Ownership |  |  | X |  | List | Train Name | Code for name of Train, as provided on the Unit Information Train tab. |  |  | R
|  | Ownership | X | X | X |  | Automatic | Resource Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name (e.g. CBY_CBYG1). |  |  | A | Resource Name (Unit Code/Mnemonic) | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS | N | N
|  | Ownership | X | X |  |  | Y/N | Joint Ownership | Does unit have multiple owners? (does not apply to CC Units, as they must have a single owner for each Train.) |  |  | R | Joint Ownership? | 1. Select from the list: Y or N 2. If N then Fixed Ownership 100% | R | Dropdown List |  |  |  | N | N
|  | Ownership | X | X | X |  | Text | Resource Entity Name | Enter the name of the Resource Entity who owns all or a portion of this unit. |  |  | C | Resource Entity Name | This field is conditional: Required if single entity represents the Resource. Data type: Character. Resource Entity Name should not allow any special characters except spaces. RE Duns# should be unique for different Owner RE's for a Jointly Owned Unit | C | Character | B,DVB | RARF Guide Version 4.0/RARF Glossary Version 4.0 | EMS,Lodestar,NMMS | N | N
|  | Ownership | X | X | X |  | Number | Resource Duns Number | Enter the name of the Resource Entity DUNS # who owns all or a portion of this unit (or Train). |  |  | C | Resource Duns Number | This field is Conditional : Required if single entity represents the Resource. This should be either 9 or 13 digit number | C | Integer | B,DVB | RARF Guide Version 4.0/RARF Glossary Version 4.0 | EMS,Lodestar,NMMS | N | N
|  | Ownership | X | X | X |  | % | Fixed Ownership | Percentage of ownership for this unit that this Resource Entity owns in decimal format. (Does not apply to CC Units, as they must have a single owner for each Train.) |  |  | C | Fixed Ownership | Sum of the Ownership percentage should be 100. Up to 4 decimal places only are valid (limit submission to 4 places after the point) | C | Numeric | B,DVB | Lin Xu/Art Deller | EMS,Lodestar,MMS,NMMS | N | N
|  | Ownership | X | X | X |  | Y/N | Master Owner | Is this Resource Entity the Master Owner of the unit? (does not apply to CC Units, as they must have a single owner for each Train.) |  |  | R | Master Owner | 1. Select from Y or N. 2. Required 3. Must select ‘Y’ for one resource entity for each unit on Split Generation Resources ( 'Y' identifies the Master Owner) | R | Dropdown List | B,DVB | RARF Glossary Version 4.0 | EMS,Lodestar,NMMS | N | N
|  | Ownership | X | X | X |  | Date | Ownership Start Date | Date this Resource Entity ownership was started |  |  | O | Ownership Start Date | Format should be: MM/DD/YYYY | R O | Date | B/DVB | Data Ag |  | N | N
|  | Ownership | X | X | X |  | Date | Ownership Stop Date | Date this Resource Entity ownership was stopped |  |  | O | Ownership Stop Date | This field is optional. Format should be: MM/DD/YYYY | O | Date | B/DVB | Data Ag |  | N | N
|  | Parameters | X | X | X |  | List | Unit Name | Code for name of generator unit, as provided on the Unit Information tab. |  |  | R | Unit Name | 1.This field is not null. Data type: Character. 2. Can not exceed 8 characters for single owner units 3. Should not allow spaces | R | Character | B | RARF Glossary Version 4.0 /RARF Guide version 4.0/ RARF Forms | Lodestar,NMMS | N | N
|  | Parameters | X | X | X |  | Automatic | Resource Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name (e.g. CBY_CBYG1). |  |  | A | Resource Name (Unit Code/Mnemonic) | 1.This field is Not null: Capture Site Code and Unit Name and prepopulate this field with Sitecode_Unit Name. 2. All letters should be capital 3. Should not allow spaces 4. Can not exceed 17 characters | R | Character | B,DVB | Angela Moy/RARF Glossary Version 4.0/RARF Guide Version 4.0/Jamil Daouk | Lodestar,NMMS | N | N
|  | Parameters | X | X | X |  | MW | High Reasonability Limit | An "Out-of-Bounds" value chosen by RE and used by ERCOT to alarm/reject data exceeding this value. Per Protocol 3.7.1, Resource Parameter Criteria, also used to validate reactive capability curves |  |  | R | High Reasonability Limit | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Limit must be > 0 3. High Reasonability Limit >= Low Reasonability Limit | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS | N | N
|  | Parameters | X | X | X |  | MW | Low Reasonability Limit | An "Out-of-Bounds" value chosen by Resource Entity and used by ERCOT to alarm/reject data below this value. Per Protocol Section 3.7.1, also used to validate reactive capability curves. |  |  | R | Low Reasonability Limit | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Limit must be >= 0 | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | MMS,NMMS | N | N
|  | Parameters | X | X | X |  | MW/min | High Reasonability Ramp Rate Limit | An "Out-of-Bounds" value chosen by Resource Entity and used by ERCOT to alarm/reject data exceeding this value, SCED is also bounded by this value. |  |  | R | High Reasonability Ramp Rate Limit | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. High Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | EMS,MMS,NMMS | N | N
|  | Parameters | X | X | X |  | MW/min | Low Reasonability Ramp Rate Limit | An "Out-of-Bounds" value chosen by Resource Entity and used by ERCOT to alarm/reject data below this value, SCED is also bounded by this value. |  |  | R | Low Reasonability Ramp Rate Limit | 1. Warning! If decimal value is submitted, then MMS will round to the first decimal place 2. Low Reasonability Ramp Rate Limit >= 0 | R | Numeric | B,DVB | KittiPong/Lin Xu/ Jamil Daouk 11/08/11 | EMS,MMS,NMMS | N | N
|  | Parameters | X | X | X |  | MW | Seasonal Net Max Sustainable Rating - Spring | Spring months are March, April, and May. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R | Seasonal Net Max Sustainable Rating - Spring | 1.Seasonal Net Max Sustainable Rating - Spring > Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS | N | N
|  | Parameters | X | X | X |  | MW | Seasonal Net Min Sustainable Rating - Spring | Spring months are March, April, and May. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R | Seasonal Net Min Sustainable Rating - Spring | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS | N | N
|  | Parameters | X | X | X |  | MW | Seasonal Net Max Emergency Rating - Spring | Spring months are March, April, and May. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R | Seasonal Net Max Emergency Rating - Spring | 1.Seasonal Net Max Emergency Rating - Spring > Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS | N | N
|  | Parameters | X | X | X |  | MW | Seasonal Net Min Emergency Rating - Spring | Spring months are March, April, and May. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R | Seasonal Net Min Emergency Rating - Spring | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS,NMMS | N | N
|  | Parameters | X | X | X |  | MW | Seasonal Net Max Sustainable Rating - Summer | Summer months are June, July, and August. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R | Seasonal Net Max Sustainable Rating - Summer | 1.Seasonal Net Max Sustainable Rating - Summer > Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS | N | N
|  | Parameters | X | X | X |  | MW | Seasonal Net Min Sustainable Rating - Summer | Summer months are June, July, and August. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R | Seasonal Net Min Sustainable Rating - Summer | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu | MMS | N | N
|  | Parameters | X | X | X |  | MW | Seasonal Net Max Emergency Rating - Summer | Summer months are June, July, and August. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R | Seasonal Net Max Emergency Rating - Summer | 1.Seasonal Net Max Emergency Rating - Summer > Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS | N | N
|  | Parameters | X | X | X |  | MW | Seasonal Net Min Emergency Rating - Summer | Summer months are June, July, and August. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R | Seasonal Net Min Emergency Rating - Summer | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS | N | N
|  | Parameters | X | X | X |  | MW | Seasonal Net Max Sustainable Rating - Fall | Fall months are September, October, and November. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R | Seasonal Net Max Sustainable Rating - Fall | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS | N | N
|  | Parameters | X | X | X |  | MW | Seasonal Net Min Sustainable Rating - Fall | Fall months are September, October, and November. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R | Seasonal Net Min Sustainable Rating - Fall | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2. Seasonal Net Min Sustainable Rating - Fall. >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS | N | N
|  | Parameters | X | X | X |  | MW | Seasonal Net Max Emergency Rating - Fall | Fall months are September, October, and November. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R | Seasonal Net Max Emergency Rating - Fall | 1.Seasonal Net Max Emergency Rating - Fall > Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS | N | N
|  | Parameters | X | X | X |  | MW | Seasonal Net Min Emergency Rating - Fall | Fall months are September, October, and November. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R | Seasonal Net Min Emergency Rating - Fall | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS | N | N
|  | Parameters | X | X | X |  | MW | Seasonal Net Max Sustainable Rating - Winter | Winter months are December, January, and February. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R | Seasonal Net Max Sustainable Rating - Winter | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS | N | N
|  | Parameters | X | X | X |  | MW | Seasonal Net Min Sustainable Rating - Winter | Winter months are December, January, and February. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R | Seasonal Net Min Sustainable Rating - Winter | 1.Seasonal Net Max Sustainable Rating - Winter > Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS | N | N
|  | Parameters | X | X | X |  | MW | Seasonal Net Max Emergency Rating - Winter | Winter months are December, January, and February. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R | Seasonal Net Max Emergency Rating - Winter | 1.Seasonal Net Max Emergency Rating - Winter > Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS | N | N
|  | Parameters | X | X | X |  | MW | Seasonal Net Min Emergency Rating - Winter | Winter months are December, January, and February. These are not the HSL/LSL or HEL/LEL values that are submitted in the COP. |  |  | R | Seasonal Net Min Emergency Rating - Winter | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit | R | Numeric | B,DVB | Lin Xu/Weihui | MMS | N | N
|  | Parameters | X | X | X |  | MW | 0°f - 120°f | Unit De-rating MW values for different temperatures. Each temperature value is a separate field. |  |  | R | 0°f | UNIT_DERATING_TEMP_VAL is Required and Numeric | O |  |  | Model Administration |  | N | N
[13 empty] | 5°f | UNIT_DERATING_TEMP_VAL is Required and Numeric | O |  |  | Model Administration |  | N | N
[13 empty] | 10°f | UNIT_DERATING_TEMP_VAL is Required and Numeric | O |  |  | Model Administration |  | N | N
[13 empty] | 15°f | UNIT_DERATING_TEMP_VAL is Required and Numeric | O |  |  | Model Administration |  | N | N
[13 empty] | 20°f | UNIT_DERATING_TEMP_VAL is Required and Numeric | O |  |  | Model Administration |  | N | N
[13 empty] | 25°f | UNIT_DERATING_TEMP_VAL is Required and Numeric | O |  |  | Model Administration |  | N | N
[13 empty] | 30°f | UNIT_DERATING_TEMP_VAL is Required and Numeric | O |  |  | Model Administration |  | N | N
[13 empty] | 35°f | UNIT_DERATING_TEMP_VAL is Required and Numeric | O |  |  | Model Administration |  | N | N
[13 empty] | 40°f | UNIT_DERATING_TEMP_VAL is Required and Numeric | O |  |  | Model Administration |  | N | N
[13 empty] | 45°f | UNIT_DERATING_TEMP_VAL is Required and Numeric | O |  |  | Model Administration |  | N | N
[13 empty] | 50°f | UNIT_DERATING_TEMP_VAL is Required and Numeric | O |  |  | Model Administration |  | N | N
[13 empty] | 55°f | UNIT_DERATING_TEMP_VAL is Required and Numeric | O |  |  | Model Administration |  | N | N
[13 empty] | 60°f | UNIT_DERATING_TEMP_VAL is Required and Numeric | O |  |  | Model Administration |  | N | N
[13 empty] | 65°f | UNIT_DERATING_TEMP_VAL is Required and Numeric | O |  |  | Model Administration |  | N | N
[13 empty] | 70°f | UNIT_DERATING_TEMP_VAL is Required and Numeric | O |  |  | Model Administration |  | N | N
[13 empty] | 75°f | UNIT_DERATING_TEMP_VAL is Required and Numeric | O |  |  | Model Administration |  | N | N
[13 empty] | 80°f | UNIT_DERATING_TEMP_VAL is Required and Numeric | O |  |  | Model Administration |  | N | N
[13 empty] | 85°f | UNIT_DERATING_TEMP_VAL is Required and Numeric | O |  |  | Model Administration |  | N | N
[13 empty] | 90°f | UNIT_DERATING_TEMP_VAL is Required and Numeric | O |  |  | Model Administration |  | N | N
[13 empty] | 95°f | UNIT_DERATING_TEMP_VAL is Required and Numeric | O |  |  | Model Administration |  | N | N
[13 empty] | 100°f | UNIT_DERATING_TEMP_VAL is Required and Numeric | O |  |  | Model Administration |  | N | N
[13 empty] | 105°f | UNIT_DERATING_TEMP_VAL is Required and Numeric | O |  |  | Model Administration |  | N | N
[13 empty] | 110°f | UNIT_DERATING_TEMP_VAL is Required and Numeric | O |  |  | Model Administration |  | N | N
[13 empty] | 115°f | UNIT_DERATING_TEMP_VAL is Required and Numeric | O |  |  | Model Administration |  | N | N
[13 empty] | 120°f | UNIT_DERATING_TEMP_VAL is Required and Numeric | O |  |  | Model Administration |  | N | N