ERCOT Nodal ICCP Communication Handbook

V0.02

May 1, 2014

Revision History

| Date | Description | Version | Author(s) |
| --- | --- | --- | --- |
| 03/26/2014 | Original Draft | V0.01 | Wei Liu |
| 05/01/2014 | Updated RTDMS client communication port | V0.02 | Wei Liu |

Table of Contents

1	Introduction	4

1.1	Glossary	4

2	ERCOT Synchrophsor System	7

3	Connecting to the ERCOT Wide Area Network	9

3.1	Network Topology Overview	9

3.2	Market Participant Site WAN Connections	10

3.3	Implementation Procedures	11

4	Synchrophasor Data Exchange Requirements	11

4.1	Synchrophasor Data Exchange Standards	11

4.2	ERCOT Synchrophasor Data Format	11

4.3	ERCOT  Synchrophasor Communication Parameter Definition	12

5	Data Available to ERCOT Market Participants	12

6	Appendix: PMU data communication request form	13

# Introduction

Phasor is a quantity with magnitude and a phase angle (with respect to a reference) that is used to represent a sinusoidal signal, such as AC voltage, AC current, and AC power. In an AC power system, power flows from a higher voltage phase angle node to a lower voltage phase angle node.

Phasor technology complements existing Supervisory Control and Data Acquisition (SCADA) systems to address the new emerging need for wide area grid monitoring and management, while continuing to use existing SCADA infrastructure for local monitoring and control. Traditional SCADA/EMS systems are based on steady state power flow analysis, and therefore cannot observe the dynamic characteristics of the power system. Phasor technology overcomes this limitation.

Phasor measurements provide time synchronized sub-second data which are ideal for real-time wide area monitoring of power system dynamics. The precise timing information of these data makes it  useful outside the confines of the local substation buses where these measurements were taken. Additionally, they improve post disturbance assessment capability using high resolution time synchronized data. While not a replacement for SCADA, the phasor infrastructure will provide a layer of backup visibility should the operator primary tools fail.

The ERCOT Nodal ICCP Communication Handbook sets practices, conventions, and fundamental parameters required for Market Participants to exchange Synchrophasor data with ERCOT. Also, included in the Handbook is a description of the physical network infrastructure ERCOT has implemented to facilitate connections between ERCOT facilities and those of the Market Participants.

The Handbook specifies important configuration and functional requirements for Synchrophasor data link implementations so that the Market Participant’s system will interoperate with ERCOT’s system. Market Participants and, if applicable, their vendors will need this information to include the required features and to build the proper delivered configuration.

The ERCOT Nodal ICCP Communication Handbook also addresses the requirements for connecting to the ERCOT Wide Area Network (WAN). Other connections, such as VPN tunneling, are not supported by ERCOT anymore.

## Glossary

| Term | Definition |
| --- | --- |
| Synchrophasor | Synchronized phasors (synchrophasors) provide a real-time measurement of electrical quantities from across a power system. Applications include wide-area control, system model validation, determining stability margins, maximizing stable system loading, islanding detection, system-wide disturbance recording, and visualization of dynamic system response. The basic system building blocks are GPS satellite-synchronized clocks, phasor measurement units (PMUs), a phasor data concentrator (PDC), communication equipment, and visualization software. |
| PMU | A phasor measurement unit (PMU) is a device which measures the electrical waves on an electricity grid, using a common time source for synchronization. Time synchronization allows synchronized real-time measurements of multiple remote measurement points on the grid. In power engineering, these are also commonly referred to as synchrophasors and are considered one of the most important measuring devices in the future of power systems. A PMU can be a dedicated device, or the PMU function can be incorporated into a protective relay or other device. |
| RTDMS | Real Time Dynamics Monitoring System (RTDMS) is a synchrophasor software application for providing real-time, wide-area situational awareness to Operators, Reliability Coordinators, Planners and Operating Engineers, as well as the capability to monitor and analyze the dynamics of the power system. RTDMS is developed by Electric Power Group (EPG). |
| PDC/ePDC | Phasor Data Concentrator (PDC) is a device that receives and time-synchronizes phasor data from multiple phasor measurement units (PMUs) to produce a real-time, time-aligned output data stream. A PDC can exchange phasor data with PDCs at other locations. Through the use of multiple PDCs, multiple layers of concentration can be implemented within an individual synchrophasor data system. ePDC is the next generation technology for PDCs. The ePDC is an open, platform independent software system, unlike hardware-based or proprietary legacy PDCs, and is available on Windows or UNIX/Linux systems. |
| ISG | Intelligent Synchrophasor Gateway (ISG) allows the third party/RTDMS clients to access the RTDMS data without directly connecting to Database. These services efficiently serve the real-time and historic data to the RTDMS client and third party applications. |
| RTDMS Client | RTDMS Client enables the user to visualize phasor measurement data by providing a wide range of displays to monitor real-time dynamics and system events within the grid. It provides operators and engineers with real-time wide area monitoring, visualization, situational awareness, metrics, alarms, events in power systems. |
| WAN | Wide Area Network. Refers to both the ERCOT MPLS Network and the ERCOT DACS Network. The MPLS Network is the primary network used by Market Participants to exchange data with ERCOT. The DACS network acts as a backup for the MPLS Network. |

# ERCOT Synchrophasor System

ERCOT implemented a Synchrophasor system based on EPG’s ePDC and RTDMS.

A PDC receives and time-synchronizes phasor data from multiple PMUs to produce a real-time, time-aligned output data stream. A PDC can exchange phasor data with PDCs at other locations. Through use of multiple PDCs, multiple layers of concentration can be implemented within an individual synchrophasor data system.

ePDC is the next generation technology for Phasor Data Concentrators (PDCs) to synchronize real-time sub-second phasor data streams for use by synchrophasor applications.

Real-Time Dynamics Monitoring System (RTDMS) is a phasor based monitoring application that offers real-time wide-area visibility, as well as monitoring and alarming functions on high resolution sub-second phasor data.

RTDMS receives the complete data stream in IEEE C37.118 format. Its driver has been designed to connect with the data source (ePDC) over a local area network, and to parse the data packets in real time by applying the appropriate scaling/offset factors that convert the data into engineering units, as well as to compute certain derived values (such as Megawatts (MW) & Megavars (MVAR)). The inbuilt Data Quality Filters are capable of removing suspect data as it is streamed to (1) the Real-Time Buffer in memory for temporary caching; (2) the Real-Time Alarm & Event Detector for real-time alarming and event detection; and (3) the long-term RTDMS Database for historical archival. The Real-Time Buffer sorts and stores data by timestamp and provides high-performance data write/read capability for downstream applications. Information from various algorithmic modules as well as third-party applications can also be simultaneously cached into this buffer via its exposed interfaces. The Real-Time Alarm & Event Detector component is responsible for processing the real- time information against a set of alarming criteria & event detection triggers, and save these results back into the Real-Time Buffer for real-time alarming within the RTDMS Client applications, the RTDMS Database for offline report, and into an alarm log as text file. In case of event detection, the RTDMS Server will automatically save pre- and post-event data into binary Event Files, which could then be loaded into the RTDMS Clients for offline forensic analysis.

ERCOT ePDC receives phasor data from TSPs through ERCOT’s WAN. Any other network protocols, such as VPN, are not supported. MPs need to open their firewall on a certain TCP port to allow the incoming inquiry data from ERCOT’s ePDC server.

ERCOT’s ePDC will initial the data link by sending requests to the remote ePDC on a particular TCP port. The remote ePDC will then accept the request and it will send back the PMU information, followed by the data stream.

The ePDC passes the received data to RTDMS via TCP. Meanwhile, all the raw data is saved into a local database as archive.

The RTDMS processes the phasor data and saves the processed data to an SQL server database.

The RTDMS clients can connect to the ISG and request the data to display it.

All Synchrophasor servers and workstations are placed in different network zones, and firewalls are implemented between zones to maintain the cyber security.

The ERCOT Synchrophasor system is currently only installed in the Taylor control center; data redundancy is not available right now. However, ERCOT will implement a redundant system in the future.

# Connecting to the ERCOT WAN

## Network Topology Overview

ERCOT has implemented a TCP/IP based WAN that supports the transfer of data between ERCOT and Market Participants. ERCOT Staff or its contractors monitor and manage the ERCOT WAN. WAN Installation and maintenance responsibility is specified in the Nodal Operating Guide Section 7, available at _____.

The ERCOT WAN will not allow the exchange of data directly between Market Participants.

The ERCOT WAN is a redundant network comprised of the following network architectures:

- Private MPLS Network; and

- Private Point-to-Point DACS Network.

Figure 1 is an overview of the ERCOT WAN.

Participant

CSU

/

DSU

CSU

/

DSU

CSU

/

DSU

Router

Router

Router

Router

DACS

Network

MPLS

Network

ERCOT Taylor

ERCOT Bastrop

Firewall

Firewall

Private Intersite Fiber

Figure 1 ERCOT WAN Overview

The MPLS network is the primary means of communicating with ERCOT. If a link on the MPLS network between ERCOT and a particular Market Participant fails, the MPLS link connecting the Market Participant through the alternate ERCOT site will be used. The DACS network will only be used if both MPLS links between ERCOT and a Market Participant fails.

## Market Participant Site WAN Connections

Figure 2 describes the equipment and connections supporting operational, engineering, and market data exchange between ERCOT and Market Participants. This Market Participant Site Diagram illustrates the essential elements of the equipment and physical layer protocols used in the Market Participant’s interface to ERCOT.  All equipment shown in Figure 2 is located at the Market Participant’s site.

CSU

/

DSU

CSU

/

DSU

Router

Router

Switch

Switch

DACS

Network

MPLS

Network

Taylor Hotline

(

FXS

)

Bastrop Hotline

(

FXS

)

Taylor OPX

(

FXS

)

Bastrop OPX

(

FXS

)

Caution: Do not use 631AR or 631WA

Power Unit

System Access

Maintenance

Dupn

Interface

Processor

Test

Interface

Memory 1

Memory 2

Memory 3

Memory 4

Packet

Interface 1

Packet

Interface 2

Packet

Interface 3

Tone-Clock

Network

Control

MSS

Disk Drive

Tape Drive

Caution: Do not use 631AR or 631WA

Power Unit

A

Fractional T

1

2

Wire

2

Wire

2

Wire

2

Wire

ERCOT PROVIDED EQUIPMENT

MARKET PARTICIPANT SITE

(

1

)

Rack Unit

=

1

.

75

in

.

(

6

)

Rack Units are required

(

with spacing

)

to support

:

(

2

)

2811

Routers

(

2

)

Visual T

1

CSU

/

CSU

Firewall

Firewall

POWER

RPS

ACTIVITY

Cisco 2600

SERIES

Cisco

2811

Router

/

Switch

POWER

RPS

ACTIVITY

Cisco 2600

SERIES

Cisco

2811

Router

/

Switch

n

e

t

w

o

r

k

s



SMART-PRO

Visual T

1

CSU

/

DSU

ERCOT EQUIPMENT RACK SPACE

n

e

t

w

o

r

k

s



SMART-PRO

Visual T

1

CSU

/

DSU

10

.

5

"

Channel Bank

M

A

R

K

E

T

P

A

R

T

I

C

I

P

A

N

T

N

E

T

W

O

R

K

Figure 2 Market Participant Site Diagram

In the network infrastructure connection, ERCOT sets its line of demarcation to be a connection between a redundant pair of Ethernet switches provided by ERCOT and the firewall provided by the Market Participant. The interface “across the line of demarcation” between the ERCOT switch and the Market Participant’s firewall is provided by a minimum Category 5 10/100 BaseT Ethernet cable. The ERCOT switches auto-negotiate for network bandwidth (10 or 100 Mbps) and Duplex (full/half).

It can be seen in Figure 2 that the ERCOT provided equipment brings the redundant infrastructure into the Market Participant’s site that is necessary to meet the reliability requirements stated in the Texas Nodal Protocols. On the Market Participant’s side of the line of demarcation, it is the Market Participant’s responsibility to provide an internal network infrastructure that also meets the Texas Nodal Protocol’s communication reliability requirements. Therefore, the Market Participant is free to choose routers, firewalls, and other network equipment that best meetsethese requiremente.

The interconnecting Ethernet Switches form a Routing LAN that supports the routing of traffic over either the MPLS network or the DACS network. Traffic from the Market Participant’s system is exchanged over this network using ICCP, Synchrophasor, HTTPS, FTP, or other Application protocols as required by the various application services. This handbook details the use of Synchrophasors only.

## Implementation Procedures

Implementation of the ERCOT WAN is defined in the ERCOT ICCP Communication Handbook. A Market Participant must use  the ERCOT WAN to transfer Synchrophasor data to ERCOT.

# Synchrophasor Data Exchange Requirements

## Synchrophasor Data Exchange Standards

Synchrophasor data acquisitions are defined in the following main IEEE standards and guides:

- C37.118.1-2011 – Measurement requirements

  - Synchrophasor measurements including frequency and rate of change of frequency

- C37.118.2-2011 – Synchrophasor communications

  - Extension of the original synchrophasor standard (2005)

- IEC 61850-90-5 – Phasor measurement communications

  - Technical Report that adds wide-area capability for phasors

- C37.242-2013 – Guide for PMU utilization

  - Installation, testing, synchronization & measurement error issues

- C37.244-2013 – Guide for PDC

  - Definitions and functions used in PDC units

## ERCOT Synchrophasor Data Format

The ERCOT Synchrophasor data format requirements are defined in the following table:

| Parameter | Value |
| --- | --- |
| Data Format | C37.118 |
| buffer Size | 30 Seconds |
| Data Rate | 30 Samples/Second |
| Max Latency | 6 Seconds |
| Min Latency | 3 Seconds |
| Time Base | 1000000 |
| Comm. Type | TCP |

## ERCOT Synchrophasor Communication Parameters Definition

These communication parameters are required by market participants to connect to the ERCOT Synchrophasor system.

Market participants should configure their firewall to allow TCP communication from the ERCOT ePDC to their ePDC on port 6000 (default port number, may change upon request).

One parameter is not defined but is very important: PMU time. All PMUs must have very good time synchronization from satellite standard time signal.

| Parameter | Value | Notes |
| --- | --- | --- |
| ePDC Server ERCOT WAN IP | 192.168.172.37 |  |
| ePDC Data Request Port | 6000 | 6000 is the default port, other ports are also allowed upon request. |
| ISG Server WAN IP | 192.168.172.36 |  |
| ISG Server Outbound Port | 808 and 80 |  |
| RTDMS Client ISG URL | 192.168.172.36/rrtdms_isg |  |

# Data Available to ERCOT Market Participants

All ERCOT PMU data will be available to all TSPs. TSP users can access the data using EPG RTDMS client. Users must send access request to ERCOT. After the request is approved, ERCOT will provide the logon username and password.

ERCOT will keep PMU archive data online for one year, and keep advanced calculation data for one month.

ERCOT currently does not support TSPs to receive all PMU data directly from the ERCOT ePDC.

# Appendix: PMU data communication request form

The form below is used for both initial communication setup and new PMU update.

| ERCOT PMU Data Communication Request Form |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Company Name: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Contact Name: |  |  |  | Phone Number: |  |  |  |  | Email Address: |  |  |  |  |
| ePDC Server WAN IP: |  |  |  |  |  |  |  |  | Port Number: |  | (Default is 6000) |  |  |
| PMU Data |  |  |  |  |  |  |  |  |  |  |  |  |  |
| # | PMU Name |  | Substation |  | Enable? |  | Base KV | Longitude |  | Latitude |  | Remote Location | Notes |
| 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 11 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 12 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 13 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 14 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 15 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 16 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 17 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 18 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 19 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 20 |  |  |  |  |  |  |  |  |  |  |  |  |  |