## Slide 1: PDCWG Report to ROS
Sydney Niemeyer Chair
NRG Energy
Don Blackburn Vice Chair
Luminant Energy
July 10, 2014

## Slide 2: PDCWG Meeting July 1, 2014
Reviewed June frequency control.
  Improved CPS1 & 2.
  Frequency Profile continues to be on the high side.
    Causes were discussed: More small high frequency “events” (small up swings in frequency). Non-conforming load MW change larger on “turn-offs” than “turn-on” would contribute to larger upswings. Must have data to prove.
    Wind turbines help with high frequency but typically not with low frequency. This keeps high frequency limited to a tighter profile on the high side.
    Two “Normal” curve profiles were suggested.
  Fewer Time Error Corrections in June.

## Slide 3: PDCWG Meeting
BAL-001-TRE
  Implementation timeline was discussed. ERCOT and TRE will meet to confirm dates.
  Resources requesting a waiver from the standard as allowed in the standard requested the process for confirming the waiver.
  RARF additional information needed for conventional steam turbines. A revision request will be written.
  Protocol and Operating Guide revisions will be needed and are being developed.

## Slide 4: PDCWG Meeting
Reviewed June 21 frequency event.
  RRS providers had 5 Resources with below expected performance.
  Non-RRS providers had 4 Resources with below expected performance.
Reviewed June 7 frequency event.
  RRS providers had 2 Resources with below expected performance.
  Non-RRS providers had 9 Resources with below expected performance, poor data or inaccurate HSLs.

## Slide 5: PDCWG Meeting
Reviewed June 23 frequency event.
  RRS providers had 4 Resources with less than expected performance.
  Non-RRS providers had 8 Resources with less than expected performance due to either on augmented energy or errors in their HSL.
Interconnection Primary Frequency Response was excellent during each event.
  -694 MW/0.1 Hz, -847 MW/0.1 Hz and -1215 MW/0.1 Hz during the 21st, 7th and 23rd events.

## Slide 6: PDCWG Meeting
ERCOT will provide the PDCWG an estimate of System Inertia data in each Frequency Disturbance Report prepared for the PDCWG.
A request for high speed frequency data on each event was requested.

## Slide 7: “New” Future Meeting Dates
August 21, 2014
September 10, 2014
October 7, 2014
November 11, 2014
December 2, 2014
  All meetings at the Met Center.

## Slide 8: ERCOT Frequency Control Report June 2014
Sydney Niemeyer NRG Energy
July 1, 2014

## Slide 9: Ercot frequency control
BAL-001 CPS 1 & 2 Performance, RMS 1 and Frequency Profile

## Slide 13
CPS1 12 Month Rolling Average = 162.86

## Slide 18
60.010 <= HZ < 60.015

## Slide 20: ERCOT Time error and time correction
Time Error History

## Slide 21: Notes
Time error values from NRG True Time device can be slightly different from ERCOT’s Time Error but the daily delta times should be accurate.

## Slide 22: Time Error Corrections
Four slow Time Error Corrections were executed in June.
Other than the days with the TECs, 3 days had positive time error.

## Slide 25
Time Correction History

## Slide 28: Ercot primary frequency response performance
BAL-003-1 Interconnection Frequency Response and Bias Measure.

## Slide 29
ERCOT Primary Frequency Response – BAL-003-1
2015 Bias and Frequency Response Measure

## Slide 30: Ercot total energy and wind production
October Total ERCOT Energy and Total Energy Production from Wind Resources.