- 6.1.3	Dynamic Disturbance Recording Equipment

Dynamic disturbance recording equipment includes digital fault recorders, certain protective relays and/or meters with dynamic disturbance recording capability that meet the requirements in Sections 6.1.3.1 and 6.1.3.3.  Dynamic disturbance recording equipment required by these Operating Guides shall be time synchronized with a Global Positioning System-based clock, or ERCOT-approved alternative, with sub-cycle (<1 microsecond) timing accuracy and performance.

6.1.3.1	Recording Requirements

Recorded electrical quantities shall be:

- Provided in IEEE C37.118 format;

- Output at a minimum data rate of 30 samples per second;

- Transmitted to a central-office phasor data concentrator via a communication link with a demonstrated annual availability of 99%, or stored locally per retention requirements in Section 6.1.3.4.

6.1.3.2	Location Requirements

The location criteria listed below shall apply to Facilities operated at or above 100 kV.  The Facility owner(s), whether a Transmission Service Provider (TSP) or Generation Entity, shall install dynamic disturbance recording equipment at the following Facilities, at a minimum:

(a)	Flexible AC Transmission System (FACTS) devices energized after January 1, 2016;

(b)	Transmission facilities identified by ERCOT as critical and necessary for wide-area visualization purposes where existing visibility is limited or constrained;

(c)	Each point of interconnection for new generating facilities over 20 MVA placed into service after January 1, 2016;

(d)	Each point of interconnection for existing generating facilities over 20 MVA that has not provided for meeting MOD-026 and MOD-027 model validation requirements via other means.

6.1.3.3	Data Recording Requirements

Recorded electrical quantities shall be sufficient to determine the following:

- For locations meeting 6.1.3.2 (a through b), three phase voltage magnitude/angle data for at least two BES transmission level bus measurements;

- For locations meeting 6.1.3.2 (a through b), three phase current magnitude/angle data for at least two BES transmission level lines;

- For locations meeting 6.1.3.2 (a through b), Frequency and df/dt data for at least two BES transmission level bus measurements;

- For locations meeting 6.1.3.2 (c through d), three phase voltage magnitude/angle data for at least one generator-interconnected bus measurement;

- For locations meeting 6.1.3.2 (c through d), three phase current magnitude/angle data for each interconnected generator over 20 MVA;

(d)	For locations meeting 6.1.3.2 (c through d), Frequency and df/dt data for at least one generator-interconnected bus measurement.

6.1.3.4	Data Retention and Reporting Requirements

Recorded electrical quantities shall be retained per the following guidelines:

- Rolling 30 calendar day window for all recorded data;

- Minimum 3 year data retention for data utilized for NERC MOD-026 or MOD-027 Reliability Standard model validation;

(c)	Minimum 3 year data retention for data recorded in the context of a ERCOT-initiated disturbance analysis or event review.