| NOGRR Number | 136 | NOGRR Title | Verifying QSE Capability to Operate in CFC |
| --- | --- | --- | --- |

| Date | August 13, 2014 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Sandra Tindall |
| E-mail Address | stindall@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-3867 |
| Cell Number |  |
| Market Segment | Not applicable. |

Comments

ERCOT submits these comments to correct the baseline language in Section 2.2.4.3, ERCOT Loss of AGC

Revised Proposed Guide Language

- 1.4	Definitions

2.2.4.3	ERCOT Loss of AGC

(1)	ERCOT has back-up facilities in place for loss of control systems.  In the event that these backup facilities also fail to perform, ERCOT shall direct a QSE providing regulation to implement Constant Frequency Control (CFC) for the duration of the control loss.  ERCOT will direct the QSE providing CFC to enter the appropriate bias into their control system.  If a QSE on CFC develops a problem with regulating room, ERCOT will order additional regulation energy from another QSE to create regulation room.

(2)	ERCOT shall conduct unannounced testing to verify a QSE’s capability to operate in CFC mode.  Only QSEs with at least 350 MW of spinning reserve room will be tested.  QSEs shall be tested at least once every three years.  At a time determined solely by ERCOT, ERCOT will direct the QSE to operate under CFC mode. Once instructed by ERCOT, the QSE will have two minutes to switch to CFC mode.  The duration of this test shall be no more than 15 minutes.  ERCOT shall maintain the list of QSEs that have successfully demonstrated their capability to operate in CFC mode.