ERCOT Planning Guide Section 6: Data/Modeling September 1, 2014

6	Data/Modeling	1

6.1	Steady-State Model Development	6-1

6.2	Dynamics Model Development	6-3

6.2.1	Dynamics Data Requirements for Resources	6-4

6.2.2	Dynamics Data Requirements for Load Resources	6-4

6.2.3	Dynamics Data Requirements for and Transmission and/or Distribution Service Providers	6-5

6.2.4 	Dynamics Data Screening and Maintenance	6-5

6.2.5 	Dynamics Data Recorder	6-6

6.3	Process for Developing Short Circuit Cases	6-6

6.4	Transmission Project Information and Tracking Report and Data Requirements	6-7

6.4.1	Transmission Project Information and Tracking Report	6-7

6.4.2	ERCOT Responsibilities	6-8

6.4.3	TSP Responsibilities	6-8

6.4.4 	Regional Transmission Plan Projects in Transmission Project Information and Tracking Report	6-8

6.5	Annual Load Data Request	6-9

6.6	Intentionally Left Blank	6-10

6.7	Data Dictionary	6-10

6.8	Resource Registration Procedures	6-10

6.8.1	Resource Registration	6-11

6.8.2	Resource Registration Process	6-11

6.9	Addition of Proposed Generation Resources to the Planning Models	6-12

6.10	Contingency Filing Requirements	6-13

# 6	Data/Modeling

6.1	Steady-State Model Development

(1)	To adequately simulate steady-state system conditions, it is necessary to establish and maintain steady-state data and simulation ready study cases in accordance with the Steady State Working Group Procedure Manual.  These case models, known as steady-state base cases, shall contain appropriate equipment characteristics and system data, and shall represent projected system conditions that provide a starting point for each required season and year.

(a)	The Annual Planning Model base cases, which represent the annual peak load conditions, as prescribed in Protocol Section 3.10.2, Annual Planning Model, shall be developed annually,  updated on a triannual basis, and may be updated as needed on an interim basis.  Each Annual Planning Model base case, triannual updates, and off-cycle updates shall be posted on the Market Information System (MIS) Secure Area and the Planning and Operations Information website to ensure availability of the most accurate steady-state base cases.

(b)	Additional steady-state base cases, such as seasonal base cases, shall also be developed annually, updated on a triannual basis, and may also be updated as needed on an interim basis.  These derivative base cases, triannual updates, and off-cycle updates shall be posted on the Planning and Operations Information website to ensure availability of the most accurate steady-state base cases.

[PGRR036: Replace paragraphs (a) and (b) above with the following upon system implementation of PR066-01, Planning Site Transition to MIS:] (a) The Annual Planning Model base cases, which represent the annual peak load conditions, as prescribed in Protocol Section 3.10.2, Annual Planning Model, shall be developed annually, updated on a triannual basis, and may be updated as needed on an interim basis. Each Annual Planning Model base case, triannual updates, and off-cycle updates shall be posted on the Market Information System (MIS) Secure Area to ensure availability of the most accurate steady-state base cases. (b) Additional steady-state base cases, such as seasonal base cases, shall also be developed annually, updated on a triannual basis, and may also be updated as needed on an interim basis. These derivative base cases, triannual updates, and off-cycle updates shall be posted on MIS Secure Area to ensure availability of the most accurate steady-state base cases.

(c)	Off-cycle updates not associated with the triannual update shall be posted in a timely manner and include:

(i)	Corrections to significant errors discovered in modeling or major changes in operation configuration that affect the steady-state base cases; or

(ii)	A significant change in the scope or timing of a transmission project or the development of a new transmission project that impacts either of the next two summer base cases.

(d)	Off-cycle updates that are posted as described in paragraphs (1)(a) through (c) above shall be in the form of a Power System Simulator for Engineering (PSS/E) formatted incremental change file.

(e)	All steady-state base cases and incremental change files on the MIS Secure Area and Planning and Operations Information website shall be available for use by Market Participants.

[PGRR036: Replace paragraph (e) above with the following upon system implementation of PR066-01, Planning Site Transition to MIS:] (e) All steady-state base cases and incremental change files on the MIS Secure Area shall be available for use by Market Participants.

(f)	The Steady State Working Group Procedure Manual describes each base case that is required to be built.  The schedule for posting all steady-state base cases shall be made available on the MIS Secure Area.

(2)	Transmission Service Providers (TSPs) and ERCOT shall develop the steady-state base cases.  The steady-state base cases are derived from the Network Operations Model to ensure consistency of key characteristics, including Ratings, impedance and connectivity for Transmission Facilities that are common between the Network Operations Model and each steady-state base case.  Minor differences between the models will occur for several reasons.  For example:

(a)	The Network Operations Model is converted from a “breaker, switch, and AC line segment” convention to an equivalent steady-state base case “bus and branch” convention.  This conversion reduces the number of breakers/switches that may be included in the steady-state base case model and may combine buses separated by breakers/switches in the Network Operations Model.

(b)	Additional detailed modeling may be added to the converted Network Operations Model for planning purposes.

(c)	Future projects are added to the converted Network Operations Model that do not exist in the Network Operations Model past the model build date used to extract a snapshot from the Network Operations Model.

(3)	Using the Network Model Management System (NMMS), ERCOT and TSPs shall create steady state models that represent current and planned system conditions from the following data elements:

(a)	Each TSP, or its Designated Agent, shall provide its respective transmission network steady-state model data, including load data.

(b)	ERCOT shall utilize the latest available Resource Entity and Private Use Network model data submitted to ERCOT by the Resource Entity and the Private Use Network owners through the Resource registration process for Resource Entities.

(c)	ERCOT shall utilize proposed Generation Resource model data provided by the Interconnecting Entity (IE) during the generation interconnection process in accordance with Section 5, Generation Resource Interconnection or Change Request.

(d)	ERCOT shall determine the operating state of Generation Resources (MW, MVAr) using a security-constrained economic dispatch tool.

(e)	ERCOT shall determine the import/export levels of asynchronous transmission interconnections based on historical data.

6.2	Dynamics Model Development

(1)	To adequately simulate dynamic and transient events in the ERCOT System, it is necessary to establish and maintain dynamics data and simulation-ready study cases representing the dynamic capability and frequency characteristics of machines and equipment connected to the ERCOT System.

(2)	Dynamics data is the network data and mathematical models required in accordance with the Reliability and Operations Subcommittee (ROS)-approved Dynamics Working Group Procedural Manual for simulation of dynamic and transient events in the ERCOT System.

(3)	For Resource Entities, dynamics data includes the data needed to represent the dynamic and transient response of Resource Entity-owned devices and/or Loads including but not limited to generating units, plants, and other equipment when connected to the ERCOT System including the data for any privately owned transmission system or collection system used to connect the Resource to the ERCOT System.

(4)	For Transmission Service Providers (TSPs), dynamics data needed to represent the dynamic and transient capability of TSP-owned devices including but not limited to Load shedding relays, protective relays, FACTS devices (e.g., DVARS, SVC, STATCOM, SMES), Direct Current Ties (DC Ties), variable-frequency transformers automatically switched shunts, and transformers with automatic load tap changers.

(5)	All dynamics data must be compatible with the current version of the planning model software as described in the Dynamics Working Group Procedural Manual.

(6)	The Facility owner shall provide appropriate dynamics data to ERCOT including the data for a planned Facility.

(7)	Dynamics data for a planned Facility will be updated by the Facility owner upon completion of the design for the Facility.

(8)	Updated dynamics data for an existing Facility shall be provided to ERCOT when field tests, inspections, or other information demonstrates that the dynamics data should be changed to accurately represent the dynamic characteristics of the Facility.

(9)	Dynamics Data is considered Protected Information pursuant to Protocol Section 1.3, Confidentiality.

(10)	Dynamics data shall be provided with the legal authority to provide the information to all TSPs.  If any of the information is considered Protected Information, the Facility owner shall indicate as such.

6.2.1	Dynamics Data Requirements for Resources

(1)	A Resource Entity shall submit new or updated dynamics data in accordance with Section 5, Generation Resource Interconnection or Change Request.  The Resource Entity shall provide all dynamics data as described in the Dynamics Working Group Procedural Manual.  The Resource Entity shall provide an accurate and appropriate model and model parameters.  Resource Entities are encouraged to use standard models to represent the Resource’s dynamic and transient capability and response.  If no appropriate standard model is available, the Resource Entity shall submit a model, model documentation, and the associated model parameters to ERCOT for inclusion in simulation-ready study cases as described in the Dynamics Working Group Procedural Manual.

(2)	A Resource Entity is responsible for tuning and validating the parameters that go into their models to ensure that the models produce an accurate representation of a device’s capability and response.  If ERCOT, the interconnecting TSP, or the Dynamics Working Group (DWG) identifies inappropriate or incomplete dynamics data, ERCOT shall take action to resolve discrepancies with the Resource Entity.

6.2.2	Dynamics Data Requirements for Load Resources

(1)	ERCOT shall provide the updated Load Resource relay models.

(2)	Load Resource relay models shall be updated as describe in the Dynamics Working Group Procedural Manual.

6.2.3	Dynamics Data Requirements for and Transmission and/or Distribution Service Providers

(1)	The owner of under-frequency Load shedding equipment shall provide necessary data to model under frequency Load shedding relays for their portion of the ERCOT System as described in the Dynamics Working Group Procedural Manual.

(2)	The owner of under voltage Load shedding equipment shall provide necessary data to model under voltage Load shedding relays for their portion of the ERCOT System as described in the Dynamics Working Group Procedural Manual.

(3)	When requested by ERCOT or a Transmission and/or Distribution Service Provider (TDSP), the owner of protective relays, control systems, and Special Protection Systems (SPSs) shall provide dynamics data needed to simulate their action.

(4)	The DWG shall document appropriate Load model data as described in the Dynamics Working Group Procedural Manual for use in dynamic simulations.

(5)	The owner of a dynamic element connected to the transmission system shall provide the dynamic data needed to simulate the action of the device in dynamic simulations to ERCOT and the TDSP to which the element is connected.  Examples of dynamic elements include, but are not limited to, static-Volt-Ampere reactive (VAr) compensators, DC Ties, variable frequency transformers, switched shunt devices, and transformers with automatic tap changers.

6.2.4 	Dynamics Data Screening and Maintenance

(1)	In order to maintain simulation-ready base cases and associated dynamics data files for use in dynamic simulations, the DWG, in consultation with ERCOT, shall perform dynamic simulations, called flat-start simulations, as described in the Dynamics Working Group Procedural Manual.

[PGRR033: Replace paragraph (1) above on January 1, 2015:] (1) In order to maintain simulation-ready base cases and associated dynamics data files for use in dynamic simulations, ERCOT, in consultation with the DWG, shall perform dynamic simulations called flat-start simulations as described in the Dynamics Working Group Procedural Manual.

(2)	The schedule for producing the flat start simulations will be reviewed annually and submitted to the ROS.

(3)	Transmission owners shall review the completeness and applicability of dynamics data used in the flat start simulation for equipment connected to their system.  The model should be appropriate for the equipment and the data shall be appropriate for the model.

(4)	ERCOT shall contact the appropriate TSP or Resource Entity to resolve any dynamics data problems, incomplete or missing data, encountered while preparing the flat start simulation.

(5)	Upon completion of each flat start simulation, ERCOT shall distribute an electronic copy of all files necessary to replicate the flat start simulation as described in the Dynamics Working Group Procedural Manual to the DWG.

(6)	ERCOT and the DWG shall document assumptions made, data created, and data changed during the creation of a flat start simulation.

(7)	ERCOT shall be responsible for storing all of the dynamics data and shall maintain a repository of dynamics data with tuned parameters and any submitted revisions.

(8)	Within 30 days of receipt, ERCOT shall forward all dynamics data received to the TSP to which the dynamics device is connected.

6.2.5 	Dynamics Data Recorder

ERCOT, in consultation with the DWG, shall prepare a list of locations, based on criteria contained in the Dynamics Working Group Procedural Manual, which require the installation of devices capable of recording ERCOT Transmission Grid events with sufficient resolution to serve as a benchmark for dynamic simulations.

6.3	Process for Developing Short Circuit Cases

This Section describes the process for the development of the short circuit cases used for planning purposes.  Section 6, Disturbance Monitoring and System Protection, of the Operating Guides describes other non-planning aspects relating to system protection and disturbance monitoring requirements.

(a)	ERCOT shall collect the short circuit data sets or data updates developed by each Transmission Service Provider (TSP) and shall compile and maintain the short circuit cases.

(b)	During the first quarter of each calendar year, ERCOT shall compile and distribute the Current Year (CY) short circuit case to the System Protection Working Group (SPWG).

(c)	During the second quarter of each calendar year, ERCOT shall compile and distribute the Future Year (FY) short circuit cases for years two through five to the SPWG.

(d)	The transmission and generation systems of each Facility owner in ERCOT shall be represented completely including positive and zero sequence data.  Generation Resource data shall be provided by the Resource Entity.

(e)	Each common bus within both the short circuit case and the corresponding steady-state load flow case shall have a matching bus name and matching bus number.  Each additional bus added to the short circuit case as necessary to perform short circuit studies shall be assigned a name and bus number that does not conflict with pre-existing names and bus numbers used in the current set of load flow cases.

(f)	The positive sequence impedance of Transmission Elements used in both the load flow and short circuit cases shall be the same.

(g)	Zero sequence data shall include mutual impedance of multi-circuit transmission lines and of adjacent circuits within the same right-of-way, unless the TSP considers such impedance to be insignificant for studies made from this data.

6.4	Transmission Project Information and Tracking Report and Data Requirements

6.4.1	Transmission Project Information and Tracking Report

(1)	The ERCOT Transmission Project and Information Tracking (TPIT) report presents the current triannual status of the transmission projects (60 kV and above) that have a material impact to the flow of power in the ERCOT System.  The TPIT report communicates the status to the stakeholders through the TPIT Database.  The TPIT Database has four primary sections:

(a)	Future Projects;

(b)	Completed Projects;

(c)	Cancelled Projects; and

(d)	Regional Transmission Plan Projects.

(2)	Transmission projects listed in the current TPIT Future Projects and Completed Project sections are generally modeled in the current set of steady-state base cases used for transmission planning studies except for, but not limited to the following exceptions:

(a)	Any project that requires Regional Planning Group (RPG) review and has not completed the review process;

(b)	Any project with a projected in-service date beyond the six-year planning horizon; or

(c)	Any project that consists of only a Special Protection System (SPS) (which is not typically modeled);

(d)	In addition, each project listing includes a data field that delineates whether that project is included in the aforementioned SSWG cases.

6.4.2	ERCOT Responsibilities

ERCOT shall prepare TPIT updates using data supplied by each Transmission Service Provider (TSP), or its Designated Agent.  ERCOT shall maintain a section within the TPIT Database that describes each data element as well as identify the Entity responsible for supplying the data within each data element.  The updated TPIT Database shall be posted triannually on the Planning and Operations Information website.  The format and schedule for data collection and verification of the TPIT Database shall be determined by ERCOT and communicated to the appropriate Market Participants in a timely manner.

[PGRR036: Replace Section 6.4.2 above with the following upon system implementation of PR066-01, Planning Site Transition to MIS:] 6.4.2 ERCOT Responsibilities ERCOT shall prepare TPIT updates using data supplied by each Transmission Service Provider (TSP), or its Designated Agent. ERCOT shall maintain a section within the TPIT Database that describes each data element as well as identify the Entity responsible for supplying the data within each data element. The updated TPIT Database shall be posted triannually on the Market Information System (MIS) Secure Area. The format and schedule for data collection and verification of the TPIT Database shall be determined by ERCOT and communicated to the appropriate Market Participants in a timely manner.

6.4.3	TSP Responsibilities

TPIT provides information on transmission projects that are included in current TSP plans or included in the Regional Transmission Plan.  Each TSP shall provide information for its transmission projects to ERCOT as outlined in the TPIT Procedures.

6.4.4 	Regional Transmission Plan Projects in Transmission Project Information and Tracking Report

Each year, with input from stakeholders, ERCOT develops a Regional Transmission Plan that identifies a set of reliability-driven and economic-driven transmission projects based on the current steady-state base cases.  Transmission projects identified in the Regional Transmission Plan are typically at varying stages within the planning process and thus, are subject to change.  When a Regional Transmission Plan project is deemed appropriate for inclusion in the steady-state base cases, the TSP shall initiate inclusion of the project in the Future Projects section of TPIT, and ERCOT shall assign a TPIT project number.  The project shall also remain in the Regional Transmission Plan section of the TPIT.

6.5	Annual Load Data Request

(1)	The Transmission and/or Distribution Service Provider (TDSP) or its Designated Agent must provide Load data each year to allow necessary ERCOT System reliability analysis and planning and to meet requirements of North American Electric Reliability Corporation (NERC).  Each TDSP or its Designated Agent is responsible for providing historical and forecasted Load data to ERCOT for all Loads connected to its system as outlined in the Annual Load Data Request Form Instructions.  Data supplied in the Annual Load Data Request (ALDR) is considered Protected Information.

(2)	Some or all of the following factors may be considered when developing Load forecast data:

(a)	Economic;

(b)	Demographic;

(c)	Customer trends;

(d)	Conservation;

(e)	Improvements in the efficiency of electrical energy uses;

(f)	Other changes in the end uses of electricity; and

(g)	Weather effects.

(3)	Each Distribution Service Provider (DSP) or its Designated Agent directly interconnected with the ERCOT Transmission Grid shall provide annual Load forecasts to ERCOT as outlined in the Annual Load Data Request Form Instructions.

(4)	For each substation not owned by either a Transmission Service Provider (TSP) or a DSP, the owner shall provide a substation Load forecast to the directly-connected TSP sufficient to allow it to adequately include that substation in its ALDR response.

(5)	The TDSP or its Designated Agent shall coordinate with the appropriate working group as described in the Annual Load Data Request Form Instructions for issues with data submissions.

(6)	Load data that is incomplete, not timely submitted on the schedule, or not in the format defined in the Annual Load Data Request Form Instructions will be considered missing data.  For these missing Load data, ERCOT shall calculate Loads based on historical data and insert these Loads into the Load flow cases during Data Set A and Data Set B annual updates.

6.6	Intentionally Left Blank

6.7	Data Dictionary

(1)	The Data Dictionary provides additional bus data that is not included in the steady-state base cases or network model data.  The Steady State Working Group Procedure Manual defines the requirements for the planning portion of the Data Dictionary.

(2)	The following items pertain to data updates:

(a)	Transmission Service Providers (TSPs) shall submit all pertinent Data Dictionary data for each bus in its transmission system for SSWG models as specified in the Steady State Working Group Procedure Manual.

(b)	ERCOT shall provide pertinent Resource Entity data for the Data Dictionary.

(c)	Interim information is provided pursuant to Section 6.4.1, Transmission Project Information and Tracking Report.  TSPs may revise bus data for the Data Dictionary as necessary to reflect changes.

(3)	ERCOT shall make available a copy of the Data Dictionary on the Planning and Operations Information website per the Steady State Working Group Procedure Manual and in accordance with the schedule posted on the Market Information System (MIS) for Annual Planning Model Data Submittal.

[PGRR036: Replace paragraph (3) above with the following upon system implementation of PR066-01, Planning Site Transition to MIS:] (3) ERCOT shall make available a copy of the ERCOT Steady State Planning Data Dictionary and contingency files on the Market Information System (MIS) Secure Area per the Steady State Working Group Procedure Manual and in accordance with the schedule posted on the MIS Secure Area for Annual Planning Model Data Submittal.

6.8	Resource Registration Procedures

In accordance with Protocol Sections 3.7, Resource Parameters, 3.10, Network Operations Modeling and Telemetry, and 16.5, Registration of a Resource Entity, a Resource Entity shall register each All-Inclusive Generation Resource with ERCOT.  The Resource Entity shall submit Resource Registration data and information through the Resource Registration process pursuant to Section 6.8.2, Resource Registration Process, and made available on the Market Information System (MIS) Public Area.

6.8.1	Resource Registration

(1)	A Resource Entity shall submit complete Resource Registration data pursuant to Section 6.8.2, Resource Registration Process,  for each All-Inclusive Generation Resource prior to inclusion in applicable ERCOT systems.

(2)	All data elements requested in the Resource Registration process will be contained in the Resource Registration Glossary.  Changes, deletions or additions to the data elements in the Resource Registration Glossary will be made in accordance with the revision process specified for the Resource Registration Glossary.

(3)	ERCOT shall post the Resource Registration Glossary on the MIS Public Area.

(4)	ERCOT shall post a detailed Resource Registration Guide on the MIS Public Area that provides detailed instructions and explanations required for Resource Registration data and shall conform to the Resource Registration Glossary.

(5)	ERCOT shall make available related documents for Resource Registration on the MIS Public Area and shall notify Market Participants when changes are made to the Resource Registration process and requirements, including Resource Registration forms, the Resource Registration Glossary, and the Resource Registration Guide.

(6)	As required by Section 5, Generation Resource Interconnection or Change Request, Generation Resources shall provide accurate initial data for inclusion in the ERCOT Network Operations Model.  The data will be used to model future generation for Steady-State Working Group (SSWG), Dynamics Working Group (DWG), and System Protection Working Group (SPWG) base cases.

6.8.2	Resource Registration Process

(1)	A Resource Entity shall submit the Resource Registration data for All-Inclusive Generation Resources as described in the Resource Registration Glossary.

(2)	Upon receipt of the Resource Registration data, ERCOT shall review the completeness and accuracy of the data submission.  ERCOT shall provide notice of acceptance and/or deficiencies to the Resource Entity.

(3)	ERCOT shall provide notice to the Resource Entity if the Resource Registration data is accepted, which is not the same as an approved Network Operations Model Change Request (NOMCR).  The acceptance of the Resource Registration data only means that the registered data moves to the next step of being converted to a NOMCR.  After acceptance and/or approval, the data is still subject to various and continuous validation processes.

(4)	If ERCOT’s notice reports deficiencies through the data submission process or through subsequent validation processes, the Resource Entity shall make necessary changes specified and re-submit the Resource Registration data as necessary, until acceptance of the total set of registered data is granted.

(5)	Upon acceptance of the Resource Registration data, ERCOT shall provide the Resource Entity with the model ready date on which the Resource Registration data will be implemented in production.  Although a model ready date has been provided, subsequent data corrections may be required as a result of validation processes.

(6)	If a Resource Entity desires that the submitted Resource Registration data become effective earlier than the schedule established in Protocol Section 3.10.1, Time Line for Network Operations Model Changes, it may submit a request for interim update as described in the Resource Registration Guide.

(7)	ERCOT shall notify each Resource Entity when applicable changes to the model are processed and implemented in accordance with Protocol Section 3.10.1.

(8)	A Resource Entity shall revise the Resource Registration data as required by this Section to reflect changes in any data related to an All-Inclusive Generation Resource.

(9)	The Resource Entity must submit updated Resource Registration data containing changes made for the reasons below for an All-Inclusive Generation Resource:

(a)	Within ten Business Days of ERCOT approval of a Net Dependable Capability test to reflect the results of the test;

(b)	Within ten Business Days of ERCOT approval of a reactive capability test to reflect the results of the test;

(c)	Within ten Business Days of a request by ERCOT to check or update specific Resource Registration data; and

(d)	Within ten Business Days of a known change to any Resource Registration data.

6.9	Addition of Proposed Generation Resources to the Planning Models

(1)	ERCOT will include a proposed Generation Resource in the base cases created and maintained by the Steady State Working Group (SSWG), the System Protection Working Group (SPWG), and the Dynamics Working Group (DWG), once the Interconnecting Entity (IE) notifies ERCOT that it has received a Texas Commission on Environmental Quality (TCEQ)-approved air permit (if necessary) and demonstrates that it has obtained water rights sufficient for plant operation (if necessary), and ERCOT receives one of the following:

(a)	A signed Standard Generation Interconnection Agreement (SGIA) from the Transmission Service Provider (TSP) and a written notice from the TSP that the IE has provided:

(i)	A notice to proceed with the construction of the interconnection; and

(ii)	The financial security required to fund the interconnection facilities; or

(b)	A public, financially binding agreement between the IE and the TSP under which the interconnection for the Generation Resource will be constructed along with:

(i)	A written notice from the TSP that the IE has provided notice to proceed with the construction of the interconnection; and

(ii)	The required financial security; or

(c)	A letter from a duly authorized official from a Municipally Owned Utility (MOU) or Electric Cooperative (EC) confirming the Entity’s intent to construct and operate a proposed Generation Resource and interconnect such Generation to its own transmission system.

(2)	The IE shall provide to ERCOT the data necessary to model the Generation Resource in the base cases created and maintained by SSWG, SPWG, and the DWG, as directed by ERCOT.

(3)	Once the IE has met these requirements, ERCOT will notify the SSWG, SPWG, and the DWG, and the proposed Generation Resource will be included in the base cases created and maintained by these working groups.

6.10	Contingency Filing Requirements

Each Transmission Service Provider (TSP), or its Designated Agent, shall provide updates to the ERCOT list of steady-state contingencies corresponding to the steady-state base cases for its existing system and planned future Transmission Facilities.  ERCOT shall post the list to the Planning and Operations Information website.  The list shall be reviewed and updated as described in the Steady State Working Group Procedure Manual.  At a minimum, the list shall contain North American Electric Reliability Corporation (NERC) Category B, C and D contingencies as described in the Steady State Working Group Procedure Manual and contingencies representing the Forced Outage of a double circuit (two circuits on the same structures in excess of 0.5 miles in length).

[PGRR036: Replace Section 6.10 above with the following upon system implementation of PR066-01, Planning Site Transition to MIS:] 6.10 Contingency Filing Requirements Each Transmission Service Provider (TSP), or its Designated Agent, shall provide updates to the ERCOT list of steady-state contingencies corresponding to the steady-state base cases for its existing system and planned future Transmission Facilities. ERCOT shall post the list to the Market Information System (MIS) Secure Area. The list shall be reviewed and updated as described in the Steady State Working Group Procedure Manual. At a minimum, the list shall contain North American Electric Reliability Corporation (NERC) Category B, C and D contingencies as described in the Steady State Working Group Procedure Manual and contingencies representing the Forced Outage of a double circuit (two circuits on the same structures in excess of 0.5 miles in length).