## Slide 1: PDCWG Report to ROS
Sydney Niemeyer Chair
NRG Energy
Don Blackburn Vice Chair
Luminant Energy
September 4, 2014

## Slide 2: PDCWG Meeting August 21
Reviewed NPRR 527 implementation and timeline. ERCOT wants to utilize new data starting Nov 1, 2014.
Reviewed BAL-001-TRE-1 implementation timeline.
  Resource applicability will follow frequency response requirements in the protocols.
  Existing exemptions from PFR will carryover with documentation.
  45% of the conventional fleet Resources already meet Governor setting requirements of R6.
Four Disturbance Reports were reviewed.
  Several Resources were repeat low providers of PFR and were providers of RRS.

## Slide 3: Future Meeting Dates
September 10, 2014
October 7, 2014
November 11, 2014
December 2, 2014
  All meetings at the Met Center.

## Slide 4: ERCOT Frequency Control Report July 2014
Sydney Niemeyer NRG Energy
August 14, 2014

## Slide 5: Ercot frequency control
BAL-001 CPS 1 & 2 Performance, RMS 1 and Frequency Profile

## Slide 9
CPS1 12 Month Rolling Average = 162.66

## Slide 14
60.010 <= HZ < 60.015

## Slide 16: ERCOT Time error and time correction
Time Error History

## Slide 17: Notes
Time error values from NRG True Time device can be slightly different from ERCOT’s Time Error but the daily delta times should be accurate.

## Slide 18: Time Error Corrections
Five slow Time Error Corrections were executed in August.
Other than the days with the TECs, no day had positive time error.

## Slide 21
Time Correction History

## Slide 24: Ercot primary frequency response performance
BAL-003-1 Interconnection Frequency Response and Bias Measure.

## Slide 25
ERCOT Primary Frequency Response – BAL-003-1
2015 Bias and Frequency Response Measure

## Slide 26
BAL-003-1 Performance to R1
R1 Present Interconnection Minimum Frequency Response Requirement: -413 MW/0.1 Hz

## Slide 27: Ercot total energy and wind production
Total ERCOT Energy and Total Energy Production from Wind Resources.