## Slide 1: Small Signal Stability (SSS) Analysis for ERCOT A Presentation To ERCOT
Presented by:
Zhihong Feng, Ph.D., P. Eng.
Manager, Power System Studies
Powertech Labs Inc.
Zhihong.Feng@powertechlabs.com
Austin, Texas
September, 2014

## Slide 2
A reasonability check of system dynamic data;
Creation of 5 transfer scenarios from each of the 2 provided base cases using voltage stability analysis of all provided NERC category B, C, and D contingencies, and all 345 kV scanned single branches;
Eigenvalue analysis for the created scenarios with contingencies similar to above;
Determination of PSS settings to provide optimal performance in the ERCOT system, including existing and newly proposed PSS;
Time-domain verifications of the effectiveness of the PSS settings for various system conditions and contingencies;
Identification of the best PMU locations for oscillation monitoring;
Discussions around load sensitivity, wind generation dynamics impact, 2012 Houston oscillations event, and 2001-2002 study.
Project Scope

## Slide 3
SSS Study Procedure
Base Data Files
and Information
PSAT and VSAT
Sanity Checks
TSAT and SSAT
Sanity Checks
Assembled
Dynamic Models
Base Power Flows
and Contingencies
Voltage Stability Analysis for
All Type B, C, and D Contingencies
Power Flows at All Transfer Limits
for Type B, C, and D Contingencies
Eigen-analysis of All Scenarios for
All Type B, C, and D Contingencies
PSS Tuning without
Adverse Effects
Best PMU Locations for Oscillation Monitoring
Time-domain Verifications
Final Corrected and Tuned Models, Information, and Recommendations

## Slide 4
Model assembly: Unique sanity checking capabilities in all programs of DSAToolsTM extensively applied to set up the appropriate models.
Worst-case power flow scenarios: Intended transfers at the highest possible levels created by VSAT capabilities.
Modal analysis: Utilization of SSAT eigenvalue analysis to render a vast amount of decoupled information ,i.e., frequency and damping of critical oscillations, mode signatures, best locations for damping controls, PSS tunings optimization, best locations for inter-area oscillation monitoring, etc.
Time-domain verifications: The above analyses greatly reduce the need for otherwise completely impractical comprehensive transient stability simulations and direct the non-linear simulations to a handful of TSAT disturbance applications under the worst conditions to provide for a high level of confidence in the results.
Robustness of the Study Process

## Slide 5
Base Power Flows
Base Case | Area |  | Generation |  | Load | 
 | Name | # | MW | MVAr | MW | MVAr
FY2018 (Peak Load) | COAST | 101 | 21224 | 4770 | 23847 | 5311
 | EAST | 102 | 12554 | 1506 | 2849 | 723
 | NORTH | 103 | 4499 | 501 | 1750 | 462
 | NORTH_CENTRA (DFW Counties) | 104 (In 104) | 18099 (8039) | 2065 (1319) | 26551 (21831) | 7502 (6237)
 | SOUTH_CENTRA | 105 | 13242 | 3332 | 13845 | 4126
 | SOUTHERN | 106 | 6837 | 951 | 5444 | 1805
 | FAR_WEST | 107 | 3101 | 372 | 3153 | 951
 | WEST | 108 | 2044 | -360 | 2283 | 675
 | Total |  | 81599 | 13136 | 79721 | 21553
HWLL2016 (High Wind, Light Load) | COAST | 101 | 9545 | 1999 | 13689 | 2477
 | EAST | 102 | 5752 | -238 | 1177 | 337
 | NORTH | 103 | 1721 | -115 | 727 | 127
 | NORTH_CENTRA (DFW Counties) | 104 | 6762 (1304) | 366 (298) | 9667 (7985) | 1976 (1659)
 | SOUTH_CENTRA | 105 | 3993 | 254 | 4934 | 1242
 | SOUTHERN | 106 | 3276 | 376 | 3338 | 826
 | FAR_WEST | 107 | 2106 | -373 | 1578 | 484
 | WEST | 108 | 4096 | -31 | 1156 | 296
 | Total |  | 37250 | 2237 | 36266 | 7765

## Slide 6
Applied Contingencies
All 345 kV single-branch outages, i.e., N-1, scanned by Powertech;
All category B contingencies, i.e., N-1, provided by ERCOT;
All category C contingencies, i.e., N-2 (or N-1-1), provided by ERCOT;
  Additional combinations of generator and branch outages (G-1-1) in SSAT only;
All category D contingencies, i.e., N-x, provided by ERCOT;
Limited number of small and large disturbances in TSAT.
Base Case | # of 345 kV Scanned Contingencies (N-1) | # of Valid Specified Contingencies |  |  | Total #
 |  | Type B (N-1) | Type C (N-2) | Type D (N-x) | 
FY2018 | 817 | 1219 | 3556 | 477 | 6069
HWLL2016 | 796 | 1220 | 3539 | 473 | 6028

## Slide 7
Applied Transfers
FY2018: Source generation scaled up versus scaling up the sink load;
HWLL2016: Source generation scaled up versus reducing sink natural gas generation;
  RGV, DFW, West, and Far West sinks hit minimum before voltage stability limit;
  A second transfer applied to these four cases by scaling up their sink loads.
Import Name | Sink Area or Zones | Participating Source Areas
Houston | Coast (101) | Far West (107), West (108), North (103), North Central (104), East (102)
Rio Grande Valley (RGV) | Southern (106) | Far West (107), West (108), North (103), North Central (104), East (102)
Dallas Fort Worth (DFW) | DFW Counties: Collin (43), Dallas (57), Denton (62), Ellis (71), Hunt (116), Kaufman (126), Johnson (129), Rockwall (199), Tarrant (220) | Far West (107, West (108), North (103), Southern (106), East (102)
West | West (108) | Far West (107), Southern (106, North (103), North Central (104), East (102)
Far West | Far West (107) | West (108), Southern (106), North (103), North Central (104), East (102)

## Slide 8
Creation of Transfer Scenarios Using VSAT
* Is Lowered to Limit Found for Type B
FY2018 VS Limits
HWLL2016 VS Limits
Transfer increases are in MW to avoid confusion of the base for %;
VS margins not applied (bus voltages and branch overloads not checked either) to create the worst-case scenarios from a damping viewpoint;
Category D contingencies may cause isolation of part of the system containing loads; hence, some limits higher than those of category B or C.
Import Name | Initial MW | Possible MW Transfer Increase |  |  | First Limiting Contingency |  | 
 | Sink | Type B | Type C | Type D | Type B | Type C | Type D
Houston | 22664 | 3500 | 1375 | 300 | Scan_44645-46500-74 | DB_ID_5545 | DB_ID_9190
RGV | 7084 | 1250 | 675 | 1725* | DB_ID_3537 | DB_ID_884 | DB_ID_17991
DFW | 21768 | 2600 | 2425 | 4350* | DB_ID_15045 | DB_ID_884 | Pre-contingency
West | 2294 | 1300 | 375 | 1925* | DB_ID_13284 | DB_ID_3020 | DB_ID_11187
Far West | 2993 | 875 | 250 | 600 | DB_ID_16053 | DB_ID_15616 | DB_ID_15961
Import Name | Initial MW | Possible MW Transfer Increase |  |  | First Limiting Contingency |  | 
 | Sink | Type B | Type C | Type D | Type B | Type C | Type D
Houston | 10863 | 2175 | 250 | 1100 | DB_ID_3416 | DB_ID_2412 | DB_ID_7803
RGV | 3338 | 1633 | 1083 | 1758* | DB_ID_3772 | DB_ID_697 | DB_ID_9296
DFW | 7972 | 4051 | 3726 | 5476* | DB_ID_3772 | DB_ID_2616 | DB_ID_6723
West | 1174 | 1875 | 1550 | 2500* | DB_ID_11101 | DB_ID_653 | DB_ID_18739
Far West | 1441 | 925 | 550 | 800 | DB_ID_14077 | DB_ID_15616 | DB_ID_18710

## Slide 9
Eigenvalue Analysis – Inter-area Modes
FY2018 Lowest Damped
HWLL2016 Lowest Damped
Voltage Stability Transfer | No Fault |  | Type B Worst Contingency |  |  | Type C Worst Contingency |  |  | Type D Worst Contingency |  | 
 | f (HZ) |  (%) | f (HZ) |  (%) | Cont. ID | f (HZ) |  (%) | Cont. ID | f (HZ) |  (%) | Cont. ID
None | 0.87 | 8.23 | 0.85 | 7.96 | DB_ID_3732 | 0.78 | 7.26 | DB_ID_2194 | 0.85 | 3.91 | DB_ID_7804
Houston | 0.86 | 8.68 | 0.84 | 8.45 | DB_ID_3732 | 0.79 | 7.49 | DB_ID_2191 | 0.85 | 3.70 | DB_ID_7804
RGV | 0.87 | 8.52 | 0.87 | 8.24 | DB_ID_3694 | 0.72 | 7.52 | DB_ID_2485 | 0.85 | 3.94 | DB_ID_7804
DFW | 0.87 | 8.13 | 0.85 | 7.83 | DB_ID_3732 | 0.78 | 6.99 | DB_ID_2191 | 0.85 | 3.92 | DB_ID_7804
West | 0.87 | 8.19 | 0.85 | 7.91 | DB_ID_3732 | 0.78 | 7.21 | DB_ID_2188 | 0.85 | 3.93 | DB_ID_7804
Far West | 0.87 | 8.20 | 0.85 | 7.92 | DB_ID_3732 | 0.78 | 7.22 | DB_ID_2197 | 0.85 | 3.93 | DB_ID_7804
Voltage Stability Transfer | No Fault |  | Type B Worst Contingency |  |  | Type C Worst Contingency |  |  | Type D Worst Contingency |  | 
 | f (HZ) |  (%) | f (HZ) |  (%) | Cont. ID | f (HZ) |  (%) | Cont. ID | f (HZ) |  (%) | Cont. ID
None | 0.84 | 9.25 | 0.84 | 8.96 | DB_ID_14189 | 0.78 | 8.21 | DB_ID_785 | 0.72 | 6.94 | DB_ID_7804
Houston | 0.80 | 8.81 | 0.79 | 8.61 | DB_ID_14134 | 0.78 | 8.20 | DB_ID_785 | 0.73 | 5.01 | DB_ID_7804
RGV | 0.88 | 8.80 | 0.86 | 8.63 | DB_ID_3732 | 0.76 | 8.45 | DB_ID_2412 | 0.73 | 6.68 | DB_ID_7804
DFW | 0.83 | 7.44 | 0.83 | 7.26 | DB_ID_3525 | 0.79 | 6.48 | DB_ID_785 | 0.72 | 6.31 | DB_ID_7804
West | 0.84 | 9.07 | 0.84 | 8.75 | DB_ID_14189 | 0.78 | 7.71 | DB_ID_785 | 0.72 | 6.79 | DB_ID_7804
Far West | 0.84 | 9.18 | 0.84 | 8.86 | DB_ID_14189 | 0.78 | 8.03 | DB_ID_785 | 0.72 | 6.89 | DB_ID_7804
Additional G-1-1, combining worst type B with either of these units:
  The most dominant unit in the mode;
  The largest unit in the system;
All damping ratios > 3% and light load better than peak load.

## Slide 10
Critical Inter-area Mode – Proposed PSS
2 new PSS proposed for the synchronous generators with maximum participation factors:
  Units of the second best plant have much less participation factors.

## Slide 11
Eigenvalue Analysis – Critical Local Mode
Full Model
Simplified 2-Plant Model
Voltage Stability Transfer | FY2018 Case |  |  |  | HWLL2016 Case |  |  | 
 | No Fault |  | Contingency DB_ID_12733 |  | No Fault |  | Contingency DB_ID_12733 | 
 | f (HZ) |  (%) | f (HZ) |  (%) | f (HZ) |  (%) | f (HZ) |  (%)
None | 1.20 | 4.74 | 0.71 | -10.28 | 1.27 | 2.95 | 0.85 | -8.47
Houston | 1.21 | 4.74 | 0.71 | -10.32 | 1.27 | 2.95 | 0.85 | -8.48
RGV | 1.20 | 4.73 | 0.71 | -10.32 | 1.27 | 2.95 | 0.85 | -8.48
DFW | 1.21 | 5.12 | 0.70 | -10.30 | 1.27 | 3.79 | 0.83 | -8.21
West | 1.20 | 4.75 | 0.71 | -10.32 | 1.27 | 2.98 | 0.85 | -8.46
Far West | 1.20 | 4.74 | 0.71 | -10.32 | 1.27 | 2.94 | 0.85 | -8.47
5 new PSS proposed for the synchronous generators of two plant with maximum participation factors:
  Units of the first plant needed for damping >3%;
  Units of the second plant needed for damping >5%.
Voltage Stability Transfer | Type D Contingency DB_ID_12733 in FY2018 |  | Type D Contingency DB_ID_12733 in HWLL2016 | 
 | f (HZ) |  (%) | f (HZ) |  (%)
None | 0.74 | -5.59 | 0.89 | 0.54
Houston | 0.74 | -5.62 | 0.88 | 0.55
RGV | 0.74 | -5.63 | 0.89 | 0.02
DFW | 0.72 | -5.36 | 0.80 | -2.05
West | 0.74 | -5.66 | 0.89 | 0.67
Far West | 0.74 | -5.61 | 0.89 | 0.63

## Slide 12
Critical Local Mode – Confirmation by July 17, 2014 Event
PMU data after loss of a unit at 5:55 PM indicated 2 local modes consistent with the 2-plant model results (before category D contingency).

## Slide 13
Phasor Measurement Unit (PMU) Placements
Three traditionally-computed free-motion eigenvector sets:
  Right eigenvector entries associated with synchronous generator rotor speeds, also known as Mode Shape (MS) or signature of the mode;
  Left eigenvector entries associated with synchronous generator rotor speeds;
  Participation Factors (PFs), i.e., products of right and left eigenvector entries.
Voltage Magnitude Mode Shape (VMMS) suits PMUs as they measure bus voltages:
  6 modes with lowest damping chosen as “Modes of Interest”;
  VMMS vectors of each mode computed by SSAT for all 345 kV buses (practical);
  All 6 vectors merged and ranked for |VMMS| > 0.5 (34 buses).

## Slide 14
Characteristics of the Selected Modes
Mode #1 mostly confined to areas 101 [COAST] & 106 [SOUTHERN].
Mode #2 not much different from mode #1:
  Mode #1 corresponds to worst type B contingency;
  Mode #2 corresponds to worst type C contingency (more severe).
Mode #3 mainly contained in area 101 [COAST];
Modes #4, #5, and #6: Light load versions of modes #1, #2, and #3.
Mode of Interest for Monitoring by PMUs |  |  | Scenario |  | Contingency | 
# | f (HZ) |  (%) | Base | Transfer | Type | ID
1 | 0.85 | 7.83 | FY2018 | DFW | B | DB_ID_3732
2 | 0.78 | 6.99 | FY2018 | DFW | C | DB_ID_2191
3 | 0.85 | 3.70 | FY2018 | Houston | D | DB_ID_7804
4 | 0.83 | 7.26 | HWLL2016 | DFW | B | DB_ID_3525
5 | 0.79 | 6.48 | HWLL2016 | DFW | C | DB_ID_785
6 | 0.73 | 5.01 | HWLL2016 | Houston | D | DB_ID_7804

## Slide 15
Best Substations for Oscillation Monitoring by PMUs
# | ¦VMMS¦ | Bus # [Name] | Weather Area # [Name] | Service Area # [Name]
1 | 1.000 | 8905 [NEDIN7C 345.] | 106 [SOUTHERN] | 8 [AEP_TCC ]
2 | 1.000 | 5915 [SO_TEX__345.] | 101 [COAST ] | 10 [STP ]
3 | 1.000 | 3100 [MARTINLK345.] | 102 [EAST ] | 1 [ONCOR_ED]
4 | 1.000 | 40600 [ROANS___345.] | 102 [EAST ] | 4 [CNP_TSP ]
5 | 0.983 | 44645 [SNGLTN_3345.] | 102 [EAST ] | 4 [CNP_TSP ]
6 | 0.934 | 967 [GIBN_CRE345.] | 102 [EAST ] | 12 [TMPA_TSP]
7 | 0.920 | 45972 [KUYDAL75345.] | 101 [COAST ] | 4 [CNP_TSP ]
8 | 0.908 | 42500 [DOW_____345.] | 101 [COAST ] | 4 [CNP_TSP ]
9 | 0.902 | 46500 [TOMBAL__345.] | 101 [COAST ] | 4 [CNP_TSP ]
10 | 0.875 | 3102 [TYLERGND345.] | 102 [EAST ] | 1 [ONCOR_ED]
11 | 0.874 | 3116 [MTENTRPR345.] | 102 [EAST ] | 1 [ONCOR_ED]
12 | 0.872 | 3109 [STRYKER_345.] | 102 [EAST ] | 1 [ONCOR_ED]
13 | 0.864 | 3105 [ELKTON_5345.] | 102 [EAST ] | 1 [ONCOR_ED]
14 | 0.863 | 45971 [KUYDAL74345.] | 101 [COAST ] | 4 [CNP_TSP ]
15 | 0.861 | 3103 [SHAMBRGR345.] | 102 [EAST ] | 1 [ONCOR_ED]
16 | 0.856 | 3119 [NACOGDSE345.] | 102 [EAST ] | 1 [ONCOR_ED]
17 | 0.848 | 46290 [RTHWOD__345.] | 101 [COAST ] | 4 [CNP_TSP ]
18 | 0.835 | 3117 [LUFKNSS_345.] | 102 [EAST ] | 1 [ONCOR_ED]
19 | 0.773 | 80307 [DELSOL7B345. | 106 [SOUTHERN] | 8 [AEP_TCC ]
20 | 0.749 | 8902 [RIOHONDO345.] | 106 [SOUTHERN] | 8 [AEP_TCC ]
21 | 0.721 | 44900 [ZENITH__345.] | 101 [COAST ] | 4 [CNP_TSP ]
22 | 0.685 | 8164 [COLETO7A345.] | 106 [SOUTHERN] | 8 [AEP_TCC ]
23 | 0.682 | 44200 [HILLJE__345.] | 101 [COAST ] | 4 [CNP_TSP ]
24 | 0.681 | 40900 [KING____345.] | 101 [COAST ] | 4 [CNP_TSP ]
25 | 0.670 | 45500 [T_H_W___345.] | 101 [COAST ] | 4 [CNP_TSP ]
26 | 0.660 | 46100 [N_BELT__345.] | 101 [COAST ] | 4 [CNP_TSP ]
27 | 0.644 | 40700 [GRNBYU__345.] | 101 [COAST ] | 4 [CNP_TSP ]
28 | 0.584 | 3130 [FOREGROV345.] | 102 [EAST ] | 1 [ONCOR_ED]
29 | 0.579 | 3124 [TRINDAD2345.] | 102 [EAST ] | 1 [ONCOR_ED]
30 | 0.568 | 3123 [TRINDAD1345.] | 102 [EAST ] | 1 [ONCOR_ED]
31 | 0.563 | 80355 [DELSOL7A345. | 106 [SOUTHERN] | 8 [AEP_TCC ]
32 | 0.560 | 43035 [OASIS___345.] | 101 [COAST ] | 4 [CNP_TSP ]
33 | 0.539 | 5966 [LALTA345345. | 106 [SOUTHERN] | 15 [BPUB TSP]
34 | 0.537 | 43030 [MEADOW__345.] | 101 [COAST ] | 4 [CNP_TSP ]

## Slide 16
Load Model Sensitivity
ERCOT-supplied load model was compared with stiffer static and partly-dynamic (complex with small motors) load models:
  For both variations, reductions in damping of critical modes may be significant but not critical;
  Insignificant after adding the recommended PSS.
Mode Description | Loading | Transfer | PL: 50%I, 50%Z QL: 50%P, 50%Z |  | PL: 100%I QL: 50%P, 50%I |  | PL: 20%SM, 80%I QL: 20%SM, 80%Z | 
 |  |  | f (HZ) |  (%) | f (HZ) |  (%) | f (HZ) |  (%)
Inter-area Mode after Type D Contingency DB_ID_7804 | FY2108 | Houston | 0.85 | 3.70 | 0.85 | 3.43 | 0.83 | 3.28
 | HWLL2016 | Houston | 0.73 | 5.01 | 0.73 | 5.66 | 0.70 | 5.78
Two-plant Mode after Type D Contingency DB_ID_12733 | FY2108 | West | 0.74 | -5.66 | 0.73 | -6.22 | 0.74 | -7.18
 | HWLL2016 | DFW | 0.80 | -2.05 | 0.80 | -2.34 | 0.79 | -1.16

## Slide 17
Wind Generation Dynamics Impact
Critical modes re-calculated after replacing all dynamic models of wind generators in two different ways:
  All corresponding units netted out, i.e., represented by negative constant-impedance loads, which are quite soft from a damping point of view;
  Each corresponding unit replaced by an infinite bus behind its source impedance, i.e., a no-dynamics equivalent for synchronous generator representation, which may be stiffer than netting in some situations.
No meaningful impact on critical eigenvalues.
Mode Description | Loading | Transfer | Dynamic Wind Generator Models |  | Netted Wind Generator Models |  | Infinite-bus wind Generator Models | 
 |  |  | f (HZ) |  (%) | f (HZ) |  (%) | f (HZ) |  (%)
Inter-area Mode after Type D Contingency DB_ID_7804 | FY2108 | Houston | 0.85 | 3.70 | 0.85 | 3.70 | 0.85 | 3.73
 | HWLL2016 | Houston | 0.73 | 5.01 | 0.73 | 4.93 | 0.78 | 4.92
Two-plant Mode after Type D Contingency DB_ID_12733 | FY2108 | West | 0.74 | -5.66 | 0.74 | -5.65 | 0.74 | -3.79
 | HWLL2016 | DFW | 0.80 | -2.05 | 0.80 | -2.40 | 0.81 | -4.63

## Slide 18
Time-domain Verification – Critical Inter-area Mode
Mode Description | Loading | Transfer | Eigenvalue Analysis |  | Prony Analysis | 
 |  |  | f (HZ) |  (%) | f (HZ) |  (%)
Inter-area Mode after Type D Contingency DB_ID_7804 | FY2108 | Houston | 0.85 | 3.70 | 0.85 | 4.56
 | HWLL2016 | Houston | 0.73 | 5.01 | 0.74 | 6.21
Small disturbance

## Slide 19
Time-domain Verification – Critical Local Mode
Mode Description | Loading | Transfer | Eigenvalue Analysis |  | Prony Analysis | 
 |  |  | f (HZ) |  (%) | f (HZ) |  (%)
Two-plant Mode after Type D Contingency DB_ID_12733 | FY2108 | West | 0.74 | -5.66 | 0.66 | -3.78
 | HWLL2016 | DFW | 0.80 | -2.05 | 0.80 | -1.26
Small disturbance

## Slide 20
Time-domain Verification – FY2018 Large Disturbance
Description | Buses with 1.0 PU ¦VMMS¦ | Buses with the Lowest ¦VMMS¦
FY2018 | First Bus at the Top Tail Second Bus at the Top Tail | First Bus at the Bottom Tail Second Bus at the Bottom Tail
High contents of oscillatory modes for buses with 1 PU VMMS, and low contents for the opposite buses.

## Slide 21
Time-domain Verifications – HWLL2016 Large Disturbance
Description | Buses with 1.0 PU ¦VMMS¦ | Buses with the Lowest ¦VMMS¦
HWLL2016 | First Bus at the Top Tail Second Bus at the Top Tail | First Bus at the Bottom Tail Second Bus at the Bottom Tail
High contents of oscillatory modes for buses with 1 PU VMMS, and low contents for the opposite buses.

## Slide 22
New PSS Tunings – Control Design Toolbox (CDT)
Associated exciters all appear to be fast and suitable.
Phase
Tuning
Sample

## Slide 23
New PSS Tunings Verification – Critical Inter-area Mode
Description | Eigenvalue Analysis |  |  |  | Prony Analysis |  |  | 
 | Without New PSS |  | With New PSS |  | Without New PSS |  | With New PSS | 
 | f (HZ) |  (%) | f (HZ) |  (%) | f (HZ) |  (%) | f (HZ) |  (%)
Inter-area Mode after Type D Contingency DB_ID_7804 in the FY2018 Houston Transfer | 0.85 | 3.7 | 0.84 | 6.20 | 0.85 | 4.56 | 0.85 | 6.73
Small disturbance

## Slide 24
New PSS Tunings Verification – Critical Local Mode
Description | Eigenvalue Analysis |  |  |  | Prony Analysis |  |  | 
 | Without New PSS |  | With New PSS |  | Without New PSS |  | With New PSS | 
 | f (HZ) |  (%) | f (HZ) |  (%) | f (HZ) |  (%) | f (HZ) |  (%)
Two-plant Mode after Type D Contingency DB_ID_12733 in the FY2018 West Transfer | 0.74 | -5.66 | 0.75 | 6.33 | 0.66 | -3.78 | 0.75 | 6.18
Small disturbance

## Slide 25
Large disturbance #1
New PSS Tunings Verification – Inter-area Mode PSS Limits

## Slide 26
New PSS Tunings Verification – Inter-area Mode PSS Effect
Large disturbance #1

## Slide 27
New PSS Tunings Verification – Local Mode PSS Limits
Large disturbance #2

## Slide 28
New PSS Tunings Verification – Local Mode PSS Effect
Large disturbance #2

## Slide 29
116 PSS2A, 25 PSS2B, 22 IEEEST, and 1 ST2CUT PSS Checked;
KS2 = T7/2H gain was wrongly set in 23 PSS2A/PSS2B;
141 PSS2A/PSS2B phase compensations tuned: 27 far from optimum;
141 PSS2A/PSS2B gain compensations tuned: 6 needed reduction;
Older PSS (IEEEST and ST2CUT) checked but not tuned;
Combination of above: 39 tuned PSS2A/PSS2B proposed;
Emphasis on removing possible adverse effects on synchronizing torques, control mode stability margins, torsional filter performances, etc. (and not on unnecessary damping increase).
Existing PSS Tunings – CDT

## Slide 30
Existing PSS Tunings – Verification
Associated exciters all appear to be fast and suitable;
Minimum damping ratios reported earlier were maintained;
Eigenvalue and time-domain small-disturbance simulations were in close agreement and both indicated adequate damping;
Two large disturbances (as before) indicated better performance after tuning, as in general the PSS performed their duties without prolonged saturated outputs and with smaller activities afterwards;
Final PSS gains may be adjusted in the field, especially those that were highly under-compensated (due to implicit higher phase compensation gain after tuning).

## Slide 31
Existing PSS Tunings Verification – Large Disturbance #1
All FY2018 PSS outputs before tuning.
All FY2018 PSS outputs after tuning.

## Slide 32
Existing PSS Tunings Verification – Large Disturbance #2
All FY2018 PSS outputs before tuning.
All FY2018 PSS outputs after tuning.

## Slide 33
Assessment of a Recent Event in Houston – Description
Multiple oscillations captured at multiple generators within the Houston region between July and September 2012 (4 incidents);
Plant X units had high MW & MVAr oscillation magnitudes;
Ramp-down of Plant X outputs reduced oscillation magnitudes;
Tripping at plant X removed the sustained oscillations in the region;
No major disturbances occurred prior to the start of oscillations;
By tuning unit 4X exciter, dynamic simulations of a snapshot case re-created the oscillatory mode at 1.2~1.8 Hz (in interplant range);
Unit 4X was not concluded as the cause, although investigating a control issue related to this unit was consistent with observations.

## Slide 34
Assessment of a Recent Event in Houston – Analysis
No such mode observed in any scenario of this project;
However, simulation results were re-produced by simply inverting the sign of KF/TF feedback loop in the EXST1 exciter of unit 4X;
Eigenvalue analysis of both FY2018 and HWLL2016 cases after this control change showed a mode ~1.3 Hz with negative damping;
Not an interplant mode, since SMIB simulation showed the same;
Mode shape points out very high, almost exclusive, observability of the oscillation in Houston region;
Time-domain simulations produced 1.2~1.3 Hz oscillation sustained at exciter limits, & magnitude depending on unit 4X initial loading;
Obviously, adding more PSS and/or tuning the existing PSS could not improve a control problem of this nature; it may be avoided by regularly performing validation field testing.

## Slide 35
Assessment of a Recent Event in Houston – Responses
Unit 4X responses to a line tripping (no fault) in FY2018:
  Black: before sign inversion in its exciter (132.3 MW loading);
  Red: after sign inversion in its exciter (132.3 MW loading);
  Blue: same as red, but with minimum initial loading (31 MW).

## Slide 36
Comparison with Previous Study of the Same Nature
A similar study was performed by Powertech in 2001-2002;
Its main findings were 2 critical inter-area modes, one north-south and one east-west, especially in 2004 peak load scenarios;
PSS in AEP_TCC area were very effective in damping these modes;
Worst contingencies occurred around the Houston – San Antonio – Corpus Christi triangle;
From 2004 case to 2018 case the peak load increased from 66.9 GW to 79.7 GW, with similar increase in generation, # of PSS dramatically increased from 50 to 164, and network significantly improved;
  Overall effects of the changes on damping are quite positive;
  Houston – San Antonio – Corpus Christi triangle is still the most critical region;
  AEP_TCC PSS don’t play a critical role anymore, as confirmed by removing them;
  However, removal of all 164 PSS in FY2018 revealed a poorly-damped inter-area mode with north-south shape and frequency close to that of 2004 case.

## Slide 37
Conclusions
Sufficient damping for N-0, N-1, and N-2 contingencies in all scenarios;
One local mode with negative damping under certain extreme contingency conditions: 5 new PSS proposed for units of two plants;
One inter-area mode with poor damping in certain extreme contingency situations: 2 new PSS recommended for 2 units;
Moderate adverse effects of transfers and load dynamics on damping (consistent with milder flows through the network due to lower loading);
Better damping in light load than in peak load for corresponding scenarios;
39 existing PSS recommended for field tuning;
34 best PMU locations proposed for oscillation monitoring;
Oscillations of the 2012 Houston event: Likely a control issue at some unit in the region (thus could not be improved by PSS);
Comparing with the 2001-2002 study:
  The same Houston – San Antonio – Corpus Christi triangle still the most critical region;
  PSS in AEP_TCC area not critical anymore;
  No negative effect on damping related to the increase in renewable generations.

## Slide 38
Recommendations for Future Studies
Guiding indicators for initiating future studies of similar nature:
  Addition/retirement of sizable generation (and generator controls);
  Significant load increases, both static (non-rotating) and dynamic;
  Major expansions/interconnections of the transmission system;
  Indication of a poorly-damped oscillation in the system by monitoring devices.
Emphasis in future studies of similar nature:
  Completeness of the dynamic data (including load models);
  Accuracy of the data, particularly for the generator excitation system models (including PSS), which can be achieved by performing field testing on generators and validating/deriving appropriate models;
  System operating conditions, including the level of wind and other renewable generations.